## Cover
Shenzhen SofarSolar Co., Ltd.
SofarSolar |  | file encoding No.: |  |  |  | Version: V1.13
|  | Type of business |  | Service category: |  | Confidentiality Level:confidential
SofarSolar Modbus communication protocol | [7 empty] | Page: No. 1PagecommonPage
SofarSolar Modbus communication protocol
Distribution range: R&D department, non-R&D process interface
version numberVersion | Revised by |  | revision date |  | Amendment reason and content Change and Reason |  | ReviewerReviewed by |  | approverApproved by
V1.00 | Chen Jiancong |  | 2019-12-05 |  | new fiction
V1.01 | Chen Jiancong |  | 2020-09-02 |  | Add register address, fault ID
V1.02 | Chen Jiancong |  | 2020-12-02 |  | Added register address and fault ID, and corrected some register attribute errors
V1.03 | Chen Jiancong |  | 2021-08-02 |  | IncreasePIDConfiguration parameters and control parameters
V1.04 | Liu Yonglai |  | 2021-08-11 |  | IncreasePLCandBLEThe configuration parameters of , increase the remote reset command, expand the number of digits of the serial number for production, increase the corresponding table of peripherals and modifyPIDThe configuration address of the newPLCheartbeat failure
V1.05 | Chen Jiancong |  | 2021-08-31 |  | Fix the problem of reactive configuration type,String open circuit alarm name changed,Increase the protocol version number
V1.06 | Chen Jiancong |  | 2021-09-09 |  | Amend the definition of the protocol version,Increase the chip code,Increase lightning protection recoverable faults
V1.07 | Chen Jiancong |  | 2021-11-03 |  | Modify the definition of anti-backflow mode, add language definition,add off-grid mode,Added upgrade target chip, added resonance fault, added serial number model error, added ODM custom area, added resonance sensitivity setting,
V1.08 | Chen Jiancong |  | 2022-03-02 |  | renewPCUevent list,Increment the internal protocol version number,add customersID, AFCIVersion number address change,Add status information table,increase the total power factor,Increase the battery protocol type,Increase the logical interface enable,IncreasePENcontrol,Increase grid overvoltage protection time high
V1.09 | Chen Jiancong |  | 2022-04-24 |  | IncreaseID15,28,93,107,136, Add PID status to 0404 address, add safety parameters, add real-time SVG power control, update PCU event list, add BDU upgrade target chip, add 2 pieces of BDU data area,
V1.10 | Ma Guoping |  | 2022-05-30 |  | Increase total read and write power generationIncrease the number of battery packs and the total number of packs to read the battery pack Fault12-BMS protection description Modify the fault bit Fault11:165-167 Delete
V1.11 | Ma Guoping |  | 2022-06-27 |  | newFault28-Fault29By default, the bit area is not enabled, the neutral-ground voltage is too high, and the PV branch software is over-current fault; new protocol version error (ARM); new dry contact control mode setting; new BOOT version number (main DSP, sub DSP) ; Added power carrier communication PLC parameter area; Added battery parameter-communication protocol 11: Action;
V1.12 | Ma Guoping |  | 2022-07-27 |  | Added MODBUS protocol, added PCU voltage and current calibration coefficients; added registers 0x11C4~0x11C8: power station communication interruption protection function registers; added fault ID164 Fault11-byte0-bit3 "PSCommFault" "Power station communication failure shutdown"; new register 0x200D: protocol setting register; total power generation is modified to write-only; address 0x1046 added battery parameters-communication protocol 11: BTS 5K and modify battery parameters-communication protocol 12: action is PCU fault bit Fault3 , Added PCU fault bit bit6: SwBusInstantOCP: bus software overcurrent; bit8: PackIDErr: PackID error;
V1.13 | Ma Guoping |  | 2022-08-31 |  | Enable reserved address, increase the reading of protocol version number(ARM/DSPM/DSPL);newFault2.byte1.bit7Neutral ground fault; newFault9.byte1.bitGrid relay failure;Added battery information area"real-time battery";new"Inverter rated power",unit0.1kW, read only;new"The total number of strings/Total number of batteries", read only;Add the number and corresponding string for the specified number of operations/battery power rating;new0x0005: solarmaxprotocol;newCTRatio setting;Added hard anti-backflow switch;Modify the Italian testS/Fdescription of;Modify the description of the fault field, and delete the repetition of the communication fault of the electric meter;Modify power carrier communicationPLCparameter area

## Protocol Description
write format
Device address | function code | register start address |  | Number of write registers |  | number of bytes written | data input |  |  |  |  | CRCcheck code
1byte | 1byte | high byte | low byte | high byte | low byte | 1byte | high byte 1 | low byte 1 | … | high byte n | low byte n | low byte | high byte
Broadcast address:0x00; Device address:1-247 . | Write function code:0x10 | [5 empty] | for32bit,64Bit registers are sent in big-endian mode unless otherwise specified. like32 The bit data transmission sequence is:byte3,byte2,byte1,byte0 |  |  |  |  | useModbus-CRC16Calculation.
write response format
Device address | function code | register start address |  | Number of write registers |  | CRCcheck code
1byte | 1byte | high byte | low byte | high byte | low byte | low byte | high byte
local address | Write function code:0x10 |  |  |  |  | useModbus-CRC16Calculation.
read format
Device address | function code | register start address |  | Read the number of registers |  | CRCcheck code
1byte | 1byte | high byte | low byte | high byte | low byte | low byte | high byte
Device address:1-247 . | Read function code:0x03 |  |  |  |  | useModbus-CRC16Calculation.
read response format
Device address | function code | data bytes | reply register data |  |  |  |  | CRCcheck code
1byte | 1byte | 1byte | high byte 1 | low byte 1 | … | high byte n | low byte n | low byte | high byte
local address | Read function code:0x03 |  | for32bit,64Bit registers are sent in big-endian mode unless otherwise specified. like32 The bit data transmission sequence is:byte3,byte2,byte1,byte0 |  |  |  |  | useModbus-CRC16Calculation.
abnormal response
Device address | function code | error code |  | CRCcheck code
1byte | 1byte | 1byte |  | low byte | high byte
local address | Abnormal function code:0x90 | see error code description |  | useModbus-CRC16Calculation.
error code
value | illustrate
1 | illegal function
2 | illegal data address
3 | illegal data value
4 | Slave device failure
7 | slave is busy
read and write properties
value | full name | illustrate
R | Readable | readable register
W | Writable | writable register
V | Volatile | Volatile registers to support frequent write operations

## Address Description
| register address | field | type | precision | unit | minimum | maximum value | read and write properties | Remark | Class of Confidentiality
Generic (0x0040-0x)
| 0040 | AddressMask_General1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0041 | [8 empty] | end user
| 0042 | [8 empty] | end user
| 0043 | [8 empty] | end user
| 0044 | Modbus_Protocol_Version | BCD16 |  |  | 1.07 | 99.99 | R | The version number of this agreement. The agreement version number corresponds to the version number in the cover of this agreement. Bits 0-7 represent the minor version number, where bits 0-3 represent the low-order version number, and bits 4-7 represent the high-order version number. 8-15 bits represent the major version number, where 8-11 bits represent the low-order version number, and 12-15 bits represent the high-order version number. Example: The value 0x1234 means the protocol version number is 12.34 | end user
| 0045 | COMM_MCU_Code | ASCII |  |  |  |  | R | Communication chip code. Refer to the chip coding specification, which is not open to the public. Example: 0x4730 means "G0" | end user
| 0046 | CTRL1_MCU_Code | ASCII |  |  |  |  | R | No. 1 control chip code. Refer to the chip coding specification, which is not open to the public. Example: 0x4730 means "G0" | end user
| 0047 | CTRL2_MCU_Code | ASCII |  |  |  |  | R | No. 2 control chip code. Refer to the chip coding specification, which is not open to the public. Example: 0x4730 means "G0" | end user
| 0048 | MCU_Code_Rsvd1
| 0049 | MCU_Code_Rsvd2
| 004A | MCU_Code_Rsvd3
| 004B | MCU_Code_Rsvd4
| 004C | MCU_Code_Rsvd5
| 004D | MCU_Code_Rsvd6
| 004E | MCU_Code_Rsvd7
| 004F | MCU_Code_Rsvd8
| 0050 | MCU_Code_Rsvd9
| 0051 | MCU_Code_Rsvd10
| 0052 | Protocol_ARM-DSPM |  |  |  | 0 | 0xFFFF | R | The upper 8 bits of the protocol version number between ARM and DSPM correspond to the protocol version number of ARM-DSPM, and the lower 8 bits correspond to the protocol version number of DSPM-ARM. Example: 0x0102 indicates that the protocol version number of ARM-DSPM is 001, and the The protocol version number is 002 | end user
| 0053 | Protocol_ARM-DSPS |  |  |  | 0 | 0xFFFF | R | The upper 8 bits of the protocol version number between ARM and DSPS correspond to the protocol version number of ARM-DSPS, and the lower 8 bits correspond to the protocol version number of DSPS-ARM. Example: 0x0203 indicates that the protocol version number of ARM-DSPS is 002, and the The protocol version number is 003
| 0054 | Protocol_DSPM-DSPS |  |  |  | 0 | 0xFFFF | R | The upper 8 bits of the protocol version number between DSPM and DSPS correspond to the protocol version number of DSPM-DSPS, and the lower 8 bits correspond to the protocol version number of DSPS-DSPM. Example: 0x0304 indicates that the protocol version number of DSPM-DSPS is 003, and the The protocol version number is 004
| 0055 | Protocol_Version_Rsvd4
| 0056 | Protocol_Version_Rsvd5
| 0057 | Protocol_Version_Rsvd6
| 0058 | Protocol_Version_Rsvd7
| 0059 | Protocol_Version_Rsvd8
| 005A | Protocol_Version_Rsvd9
| 005B | Protocol_Version_Rsvd10
| 005C | Protocol_Version_Rsvd11
| 005D | Protocol_Version_Rsvd12
| 005E | Protocol_Version_Rsvd13
| 005F | Protocol_Version_Rsvd14
| 0060 | Protocol_Version_Rsvd15
| 0061 | Protocol_Version_Rsvd16
| 0062 | Protocol_Version_Rsvd17
| 0063 | Protocol_Version_Rsvd18
| 0064 | Protocol_Version_Rsvd19
| 0065 | Protocol_Version_Rsvd20
0066
0067
0068
0069
006A
006B
006C
006D
006E
006F
0070
0071
0072
0073
0074
0075
0076
0077
0078
0079
007A
007B
007C
007D
| 007E | Customer ID_0 | [5 empty] | RW | To distinguish the IDs used by different customers, refer to the customer code specification. Customer ID_0: is used to mark the customer ID. For example, the default first flight is 0x0000. For example: Tianhe 0x0001, Skyworth 0x0002, etc. | end user
| 007F | Customer ID_1 | [5 empty] | RW | Client ID_1: Alternate Extension | end user
Real-time data area (0x0400-0x07FF) | [10 empty] | total number of registers
System Information (0x0400-0x047F) | [10 empty] | 1977
| 0400 | AddressMask_Realtime_SysInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user | Shadow registers: All operations that require writing to multiple addresses at once, use shadow registers as caches. The value written to the shadow register will not take effect until the relevant control register is written.
| 0401 | [8 empty] | end user | Write control register: For all registers that cannot take effect immediately after being written, use the write control register. When reading this register, the state of the last operation is returned.
| 0402 | [8 empty] | end user
| 0403 | [8 empty] | end user
| 0404 | SysState | U16 |  |  |  |  | R | Operating status 0 : wait state 1 : Detection status 2 : Grid-connected state 3 : Emergency power supply status 4 : Recoverable fault state 5Permanent fault state 6 : upgrade status 7: Self-charging state 8: SVG state 9: PID state | end user
| 0405 | Fault1 | U16 |  |  |  |  | R | Fault Information Sheet1 | end user
| 0406 | Fault2 | U16 |  |  |  |  | R | Fault Information Sheet2 | end user
| 0407 | Fault3 | U16 |  |  |  |  | R | Fault Information Sheet3 | end user
| 0408 | Fault4 | U16 |  |  |  |  | R | Fault Information Sheet4 | end user
| 0409 | Fault5 | U16 |  |  |  |  | R | Fault Information Sheet5 | end user
| 040A | Fault6 | U16 |  |  |  |  | R | Fault Information Sheet6 | end user
| 040B | Fault7 | U16 |  |  |  |  | R | Fault Information Sheet7 | end user
| 040C | Fault8 | U16 |  |  |  |  | R | Fault Information Sheet8 | end user
| 040D | Fault9 | U16 |  |  |  |  | R | Fault Information Sheet9 | end user
| 040E | Fault10 | U16 |  |  |  |  | R | Fault Information Sheet10 | end user
| 040F | Fault11 | U16 |  |  |  |  | R | Fault Information Sheet11 | end user
| 0410 | Fault12 | U16 |  |  |  |  | R | Fault Information Sheet12 | end user
| 0411 | Fault13 | U16 |  |  |  |  | R | Fault Information Sheet13 | end user
| 0412 | Fault14 | U16 |  |  |  |  | R | Fault Information Sheet14 | end user
| 0413 | Fault15 | U16 |  |  |  |  | R | Fault Information Sheet15 | end user
| 0414 | Fault16 | U16 |  |  |  |  | R | Fault Information Sheet16 | end user
| 0415 | Fault17 | U16 |  |  |  |  | R | Fault Information Sheet17 | end user
| 0416 | Fault18 | U16 |  |  |  |  | R | Fault Information Sheet18 | end user
| 0417 | countdown | U16 | 1 | second |  |  | R | Start countdown | end user
| 0418 | Temperature_Env1 | I16 | 1 | °C |  |  | R | ambient temperature1 | end user
| 0419 | Temperature_Env2 | I16 | 1 | °C |  |  | R | ambient temperature2 | end user
| 041A | Temperature_HeatSink1 | I16 | 1 | °C |  |  | R | Radiator temperature1 | end user
| 041B | Temperature_HeatSink2 | I16 | 1 | °C |  |  | R | Radiator temperature2 | end user
| 041C | Temperature_HeatSink3 | I16 | 1 | °C |  |  | R | Radiator temperature3 | end user
| 041D | Temperature_HeatSink4 | I16 | 1 | °C |  |  | R | Radiator temperature4 | end user
| 041E | Temperature_HeatSink5 | I16 | 1 | °C |  |  | R | Radiator temperature5 | end user
| 041F | Temperature_HeatSink6 | I16 | 1 | °C |  |  | R | Radiator temperature6 | end user
| 0420 | Temperature_Inv1 | I16 | 1 | °C |  |  | R | Module temperature1 | end user
| 0421 | Temperature_Inv2 | I16 | 1 | °C |  |  | R | Module temperature2 | end user
| 0422 | Temperature_Inv3 | I16 | 1 | °C |  |  | R | Module temperature3 | end user
| 0423 | Temp_Rsvd1 | I16 | 1 | °C |  |  | R | Reserve temperature1 | end user
| 0424 | Temp_Rsvd2 | I16 | 1 | °C |  |  | R | Reserve temperature2 | end user
| 0425 | Temp_Rsvd3 | I16 | 1 | °C |  |  | R | Reserve temperature3 | end user
| 0426 | GenerationTime_Today | U16 | 1 | minute |  |  | R | Generation time of the day | end user
| 0427 | GenerationTime_Total | U32 | 1 | minute |  |  | R | total power generation time | end user
| 0428 | [8 empty] | end user
| 0429 | ServiceTime_Total | U32 | 1 | minute |  |  | R | total running time | end user
| 042A | [8 empty] | end user
| 042B | InsulationResistance | U16 | 1 | kΩ |  |  | R | Insulation resistance | end user
| 042C | SysTime_Year | U16 |  |  |  |  | R | system time-years | end user
| 042D | SysTime_Month | U16 |  |  |  |  | R | system time-month | end user
| 042E | SysTime_Date | U16 |  |  |  |  | R | system time-day | end user
| 042F | SysTime_Hour | U16 |  |  |  |  | R | system time-Hour | end user
| 0430 | SysTime_Minute | U16 |  |  |  |  | R | system time-minute | end user
| 0431 | SysTime_Second | U16 |  |  |  |  | R | system time-second | end user
| 0432 | Fault19 | U16 |  |  |  |  | R | Fault Information Sheet19 | end user
| 0433 | Fault20 | U16 |  |  |  |  | R | Fault Information Sheet20 | end user
| 0434 | Fault21 | U16 |  |  |  |  | R | Fault Information Sheettwenty one | end user
| 0435 | Fault22 | U16 |  |  |  |  | R | Fault Information Sheettwenty two | end user
| 0436 | Fault23 | U16 |  |  |  |  | R | Fault Information Sheettwenty three | end user
| 0437 | Fault24 | U16 |  |  |  |  | R | Fault Information Sheettwenty four | end user
| 0438 | Fault25 | U16 |  |  |  |  | R | Fault Information Sheet25 | end user
| 0439 | Fault26 | U16 |  |  |  |  | R | Fault Information Sheet26 | end user
| 043A | Fault27 | U16 |  |  |  |  | R | Fault Information Sheet27 | end user
| 043B | Fault28 | U16 |  |  |  |  | R | Fault Information Sheet28 | end user
| 043C | Fault29 | U16 |  |  |  |  | R | Fault Information Sheet29 | end user
| 043D | Fault30 | U16 |  |  |  |  | R | Fault Information Sheet30 | end user
043E
043F
| 0440 | AddressMask_Realtime_SysInfo2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0441 | [8 empty] | end user
| 0442 | [8 empty] | end user
| 0443 | [8 empty] | end user
| 0444 | Production_Code | U16 | [5 empty] | reserve
| 0445 | Serial_Number0 | ASCII |  |  |  |  | R | serial number1,2bit. register high8bit to store the serial number1bit; register low8bit to store the serial number2bit. | end user
| 0446 | Serial_Number1 | ASCII |  |  |  |  | R | serial number3,4bit. register high8bit to store the serial number3bit; register low8bit to store the serial number4bit. | end user
| 0447 | Serial_Number2 | ASCII |  |  |  |  | R | serial number5,6bit. register high8bit to store the serial number5bit; register low8bit to store the serial number6bit. | end user
| 0448 | Serial_Number3 | ASCII |  |  |  |  | R | serial number7,8bit. register high8bit to store the serial number7bit; register low8bit to store the serial number8bit. | end user
| 0449 | Serial_Number4 | ASCII |  |  |  |  | R | serial number9,10bit. register high8bit to store the serial number9bit; register low8bit to store the serial number10bit. | end user
| 044A | Serial_Number5 | ASCII |  |  |  |  | R | serial number11,12bit. register high8bit to store the serial number11bit; register low8bit to store the serial number12bit. | end user
| 044B | Serial_Number6 | ASCII |  |  |  |  | R | serial number13,14bit. register high8bit to store the serial number13bit; register low8bit to store the serial number14bit. | end user
| 044C | Serial_Number7 | ASCII |  |  |  |  | R | The 15th and 16th digits of the serial number. The upper 8 bits of the register store the 15th bit of the serial number; the lower 8 bits of the register store the 16th bit of the serial number. | end user
| 044D | Hardware_Version0 | ASCII |  |  |  |  | R | hardware version number1,2bit. register high8bit to store the serial number1bit; register low8bit to store the serial number2bit. | end user
| 044E | Hardware_Version1 | ASCII |  |  |  |  | R | hardware version number3,4bit. register high8bit to store the serial number3bit; register low8bit to store the serial number4bit. | end user
| 044F | Software_Version_Stage_COM | ASCII |  |  |  |  | R | Communication chip software version number stage definition bit. register low8bit storageASCIIcode. The default for the official version is'V'. | end user
| 0450 | Software_Version_Major_COM | ASCII |  |  |  |  | R | The main version number of the communication chip software. The main version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0451 | Software_Version_Custom_COM | ASCII |  |  |  |  | R | Communication chip software non-standard customized version number. The version number of the positive standard software is"00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits. | end user
| 0452 | Software_Version_Minor_COM | ASCII |  |  |  |  | R | Communication chip software subversion number. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0453 | Software_Version_Stage_Master | ASCII |  |  |  |  | R | Main controller chip software version number stage definition bit. register low8bit storageASCIIcode. The default for the official version is'V'. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits. | end user
| 0454 | Software_Version_Major_Master | ASCII |  |  |  |  | R | Main controller chip software main version number. The main version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0455 | Software_Version_Custom_Master | ASCII |  |  |  |  | R | The non-standard customized version number of the main controller chip software. The version number of the positive standard software is"00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits. | end user
| 0456 | Software_Version_Minor_Master | ASCII |  |  |  |  | R | Main controller chip software subversion number. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0457 | Software_Version_Stage_Slave | ASCII |  |  |  |  | R | Sub-controller chip software version number stage definition bit. register low8bit storageASCIIcode. The default for the official version is'V'. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits. | end user
| 0458 | Software_Version_Major_Slave | ASCII |  |  |  |  | R | Sub-controller chip software main version number. The main version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0459 | Software_Version_Custom_Slave | ASCII |  |  |  |  | R | Sub-controller chip software non-standard customized version number. The version number of the positive standard software is"00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits. | end user
| 045A | Software_Version_Minor_Slave | ASCII |  |  |  |  | R | Sub-version number of the sub-controller chip software. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 045B | Safety_Version_Major | U16 |  |  |  |  | R | The main version number of the safety library | end user
| 045C | Safety_version_Minor | U16 |  |  |  |  | R | Safety library subversion number | end user
| 045D | Boot_Version_COM | U16 |  |  |  |  | R |  | end user
| 045E | Boot_Version_Master | U16 |  |  |  |  | R | hostDSPofBOOTversion number | end user
| 045F | Boot_Version_Slave | U16 |  |  |  |  | R | viceDSPofBOOTversion number | end user
| 0460 | Safety_Firmware_Version_Stage | ASCII |  |  |  |  | R | The stage definition bit of the safety certification software version number. The lower 8 bits of the register store the ASCII code. The default value for official versions is 'V'. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0461 | Safety_Firmware_Version_Major | ASCII |  |  |  |  | R | The main version number of the safety certification software. The main version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0462 | Safety_Firmware_Version_Custom | ASCII |  |  |  |  | R | Non-standard customized version number of safety certification software. The version number of the positive standard software is"00"The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits. | end user
| 0463 | Safety_Firmware_Version_Minor | ASCII |  |  |  |  | R | The subversion number of the safety certification software. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number. | end user
| 0464 | Safety_Hardware_Version0 | ASCII |  |  |  |  | R | Safety certification hardware version number No.1,2bit. register high8bit to store the serial number1bit; register low8bit to store the serial number2bit. | end user
| 0465 | Safety_Hardware_Version1 | ASCII |  |  |  |  | R | Safety certification hardware version number No.3,4bit. register high8bit to store the serial number3bit; register low8bit to store the serial number4bit. | end user
| 0466 | Afci_Ver_Firmware | ASCII |  |  |  |  | R | afciFirmware version number 'V'high8bit reserved;Low8Bit holds the version number.
| 0467 | Afci_Ver_Sft | ASCII |  |  |  |  | R | afciSoftware versionhigh8bit storage1bit;Low8bit storage2bit.
| 0468 | Afci_Ver_Hard | ASCII |  |  |  |  | R | afcihardware versionhigh8bit storage1bit;Low8bit storage2bit.
| 0469 | Afci_Srs_Hard | ASCII |  |  |  |  | R | afcihardware serial numberhigh8bit storage1bit;Low8bit storage2bit.
| 046A | Afci_Ver_Com | ASCII |  |  |  |  | R | afciCommunication versionhigh8bit storage1bit;Low8bit storage2bit.
046B
046C
046D
046E
046F
| 0470 | Serial_Number8 | ASCII |  |  |  |  | R | The 17th and 18th digits of the serial number. The upper 8 bits of the register store the 17th bit of the serial number; the lower 8 bits of the register store the 18th bit of the serial number. | end user
| 0471 | Serial_Number9 | ASCII |  |  |  |  | R | The 19th and 20th digits of the serial number. The upper 8 bits of the register store the 19th bit of the serial number; the lower 8 bits of the register store the 20th bit of the serial number. | end user
| 0472 | Serial_Number11_Rsvd0 | ASCII |  |  |  |  | R
| 0473 | Serial_Number11_Rsvd1 | ASCII |  |  |  |  | R
| 0474 | Serial_Number12_Rsvd2 | ASCII |  |  |  |  | R
| 0475 | Serial_Number13_Rsvd3 | ASCII |  |  |  |  | R
| 0476 | Serial_Number14_Rsvd4 | ASCII |  |  |  |  | R
| 0477 | State1 | U16 |  |  |  |  | R | Status Information Table 1 | end user
| 0478 | State2 | U16 |  |  |  |  | R | Status Information Table 2 | end user
| 0479 | State3 | U16 |  |  |  |  | R | Status Information Table 3 | end user
| 047A | State4 | U16 |  |  |  |  | R | Status Information Table 4 | end user
| 047B | State5 | U16 |  |  |  |  | R | Status Information Table 5 | end user
| 047C | State6 | U16 |  |  |  |  | R | Status Information Table 6 | end user
| 047D | State7 | U16 |  |  |  |  | R | Status Information Table 7 | end user
| 047E | State8 | U16 |  |  |  |  | R | Status Information Table 8 | end user
| 047F | State9 | U16 |  |  |  |  | R | Status Information Table 9 | end user
Grid-connected output (0x0480-0x04FF)
| 0480 | AddressMask_Realtime_GridOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0481 | [8 empty] | end user
| 0482 | [8 empty] | end user
| 0483 | [8 empty] | end user
| 0484 | Frequency_Grid | U16 | 0.01 | Hz |  |  | R | grid frequency | end user
| 0485 | ActivePower_Output_Total | I16 | 0.01 | kW |  |  | R | total active power. Discharge is positive, charge is negative | end user
| 0486 | ReactivePower_Output_Total | I16 | 0.01 | kW |  |  | R | total reactive power. Inverter side lead is positive, lag is negative | end user
| 0487 | ApparentPower_Output_Total | I16 | 0.01 | kW |  |  | R | total apparent power. Discharge is positive, charge is negative | end user
| 0488 | ActivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | totalPCCActive power. Selling electricity is positive, buying electricity is negative | end user
| 0489 | ReactivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | totalPCCreactive power. Inverter side lead is positive, lag is negative | end user
| 048A | ApparentPower_PCC_Total | I16 | 0.01 | kW |  |  | R | totalPCCinspecting power. Selling electricity is positive, buying electricity is negative | end user
| 048B | GridOutput_Rsvd1 | [5 empty] | R | Grid output reservation1 | end user
| 048C | GridOutput_Rsvd2 | [5 empty] | R | Grid output reservation2 | end user
| 048D | Voltage_Phase_R | U16 | 0.1 | V |  |  | R | R-phase grid voltage | end user
| 048E | Current_Output_R | U16 | 0.01 | A |  |  | R | RPhase inverter output current | end user
| 048F | ActivePower_Output_R | I16 | 0.01 | kW |  |  | R | RThe phase inverter outputs active power. Discharge is positive, charge is negative | end user
| 0490 | ReactivePower_Output_R | I16 | 0.01 | kW |  |  | R | RThe phase inverter outputs reactive power. Inverter side lead is positive, lag is negative | end user
| 0491 | PowerFactor_Output_R | I16 | 0.001 | pu |  |  | R | RPhase power factor. Inverter side lead is positive, lag is negative | end user
| 0492 | Current_PCC_R | U16 | 0.01 | A |  |  | R | RMutuallyPCCcurrent | end user
| 0493 | ActivePower_PCC_R | I16 | 0.01 | kW |  |  | R | RMutuallyPCCActive power | end user
| 0494 | ReactivePower_PCC_R | I16 | 0.01 | kW |  |  | R | RMutuallyPCCreactive power. Inverter side lead is positive, lag is negative | end user
| 0495 | PowerFactor_PCC_R | I16 | 0.001 | pu |  |  | R | RMutuallyPCCpower factor. Inverter side lead is positive, lag is negative | end user
| 0496 | R_Rsvd1 | [5 empty] | R | RPhase reservation1 | end user
| 0497 | R_Rsvd2 | [5 empty] | R | RPhase reservation2 | end user
| 0498 | Voltage_Phase_S | U16 | 0.1 | V |  |  | R | S-phase grid voltage | end user
| 0499 | Current_Output_S | U16 | 0.01 | A |  |  | R | S-phase inverter output current | end user
| 049A | ActivePower_Output_S | I16 | 0.01 | kW |  |  | R | SThe phase inverter outputs active power. Discharge is positive, charge is negative | end user
| 049B | ReactivePower_Output_S | I16 | 0.01 | kW |  |  | R | SThe phase inverter outputs reactive power. Inverter side lead is positive, lag is negative | end user
| 049C | PowerFactor_Output_S | I16 | 0.001 | pu |  |  | R | SPhase power factor. Inverter side lead is positive, lag is negative | end user
| 049D | Current_PCC_S | U16 | 0.01 | A |  |  | R | S-phase PCC current | end user
| 049E | ActivePower_PCC_S | I16 | 0.01 | kW |  |  | R | SMutuallyPCCActive power. Discharge is positive, charge is negative | end user
| 049F | ReactivePower_PCC_S | I16 | 0.01 | kW |  |  | R | SMutuallyPCCreactive power. Inverter side lead is positive, lag is negative | end user
| 04A0 | PowerFactor_PCC_S | I16 | 0.001 | pu |  |  | R | SMutuallyPCCpower factor. Inverter side lead is positive, lag is negative | end user
| 04A1 | S_Rsvd1 | [5 empty] | R | SPhase reservation1 | end user
| 04A2 | S_Rsvd2 | [5 empty] | R | SPhase reservation2 | end user
| 04A3 | Voltage_Phase_T | U16 | 0.1 | V |  |  | R | T-phase grid voltage | end user
| 04A4 | Current_Output_T | U16 | 0.01 | A |  |  | R | T-phase inverter output current | end user
| 04A5 | ActivePower_Output_T | I16 | 0.01 | kW |  |  | R | TThe phase inverter outputs active power. Discharge is positive, charge is negative | end user
| 04A6 | ReactivePower_Output_T | I16 | 0.01 | kW |  |  | R | TThe phase inverter outputs reactive power. Inverter side lead is positive, lag is negative | end user
| 04A7 | PowerFactor_Output_T | I16 | 0.001 | pu |  |  | R | TPhase power factor. Inverter side lead is positive, lag is negative | end user
| 04A8 | Current_PCC_T | U16 | 0.01 | A |  |  | R | T-phase PCC current | end user
| 04A9 | ActivePower_PCC_T | I16 | 0.01 | kW |  |  | R | TMutuallyPCCActive power. Discharge is positive, charge is negative | end user
| 04AA | ReactivePower_PCC_T | I16 | 0.01 | kW |  |  | R | TMutuallyPCCreactive power. Inverter side lead is positive, lag is negative | end user
| 04AB | PowerFactor_PCC_T | I16 | 0.001 | pu |  |  | R | TMutuallyPCCpower factor. Inverter side lead is positive, lag is negative | end user
| 04AC | T_Rsvd1 | [5 empty] | R | TPhase reservation1 | end user
| 04AD | T_Rsvd2 | [5 empty] | R | TPhase reservation2 | end user
| 04AE | ActivePower_PV_Ext | U16 | 0.01 | kW |  |  | R | External power generation | end user
| 04AF | ActivePower_Load_Sys | U16 | 0.01 | kW |  |  | R | Total system load power | end user
| 04B0 | Voltage_Phase_L1N | U16 | 0.1 | V |  |  | R | gridL1rightNVoltage RMS | end user
| 04B1 | Current_Output_L1N | U16 | 0.01 | A |  |  | R | L1RMS output current | end user
| 04B2 | ActivePower_Output_L1N | I16 | 0.01 | kW |  |  | R | L1Online output active power | end user
| 04B3 | Current_PCC_L1N | U16 | 0.01 | A |  |  | R | L1on-lineCTCurrent RMS | end user
| 04B4 | ActivePower_PCC_L1N | I16 | 0.01 | kW |  |  | R | L1on-linePCCActive power | end user
| 04B5 | Voltage_Phase_L2N | U16 | 0.1 | V |  |  | R | gridL2rightNVoltage RMS | end user
| 04B6 | Current_Output_L2N | U16 | 0.01 | A |  |  | R | L2RMS output current | end user
| 04B7 | ActivePower_Output_L2N | I16 | 0.01 | kW |  |  | R | L2Online output active power | end user
| 04B8 | Current_PCC_L2N | U16 | 0.01 | A |  |  | R | L2on-lineCTCurrent RMS | end user
| 04B9 | ActivePower_PCC_L2N | I16 | 0.01 | kW |  |  | R | L2Online output active power | end user
| 04BA | Voltage_Line_L1 | U16 | 0.1 | V |  |  | R | L1Line Voltage:R/Svoltage between phases | end user
| 04BB | Voltage_Line_L2 | U16 | 0.1 | V |  |  | R | L2Line Voltage:S/Tvoltage between phases | end user
| 04BC | Voltage_Line_L3 | U16 | 0.1 | V |  |  | R | L3Line Voltage:T/Rvoltage between phases | end user
| 04BD | Power_Factor | I16 | 0.001 | pu |  |  | R | total power factor. Inverter side lead is positive, lag is negative | end user
04BE
04BF
04C0
04C1
04C2
04C3
04C4
04C5
04C6
04C7
04C8
04C9
04CA
04CB
04CC
04CD
04CE
04CF
04D0
04D1
04D2
04D3
04D4
04D5
04D6
04D7
04D8
04D9
04DA
04DB
04DC
04DD
04DE
04DF
04E0
04E1
04E2
04E3
04E4
04E5
04E6
04E7
04E8
04E9
04EA
04EB
04EC
04ED
04EE
04EF
04F0
04F1
04F2
04F3
04F4
04F5
04F6
04F7
04F8
04F9
04FA
04FB
04FC
04FD
04FE
04FF
Off-grid output (0x0500-0x057F)
| 0500 | AddressMask_Realtime_EmergencyOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0501 | [8 empty] | end user
| 0502 | [8 empty] | end user
| 0503 | [8 empty] | end user
| 0504 | ActivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load active power. Load consumption is positive and feedback is negative. | end user
| 0505 | ReactivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load reactive power | end user
| 0506 | ApparentPower_Load_Total | I16 | 0.01 | kW |  |  | R | Load apparent power. Load consumption is positive and feedback is negative. | end user
| 0507 | Frequency_Output | U16 | 0.01 | Hz |  |  | R | output voltage frequency | end user
| 0508 | ESOutput_Rsvd1 | [5 empty] | R | Off-grid total output reserved 1 | end user
| 0509 | ESOutput_Rsvd2 | [5 empty] | R | Off-grid total output reserved 2 | end user
| 050A | Voltage_Output_R | U16 | 0.1 | V |  |  | R | RPhase inverter output voltage | end user
| 050B | Current_Load_R | I16 | 0.01 | A |  |  | R | RPhase load current | end user
| 050C | ActivePower_Load_R | I16 | 0.01 | kW |  |  | R | RPhase load active power. Load consumption is positive and feedback is negative. | end user
| 050D | ReactivePower_Load_R | I16 | 0.01 | kW |  |  | R | RPhase load reactive power. Inverter side lead is positive, lag is negative | end user
| 050E | ApparentPower_Load_R | I16 | 0.01 | kVA |  |  | R | RPhase load apparent power. Load consumption is positive and feedback is negative. | end user
| 050F | LoadPeakRatio_R | U16 | 0.01 | pu |  |  | R | RPhase load peak ratio | end user
| 0510 | Voltage_Load_R | U16 | 0.1 | V |  |  | R | RCorresponding emergency load voltage | end user
| 0511 | ESR_Rsvd2 | [5 empty] | R | RPhase reservation2 | end user
| 0512 | Voltage_Output_S | U16 | 0.1 | V |  |  | R | SPhase inverter output voltage | end user
| 0513 | Current_Load_S | I16 | 0.01 | A |  |  | R | SPhase load current | end user
| 0514 | ActivePower_Load_S | I16 | 0.01 | kW |  |  | R | SPhase load active power. Load consumption is positive and feedback is negative. | end user
| 0515 | ReactivePower_Load_S | I16 | 0.01 | kW |  |  | R | SPhase load reactive power. Inverter side lead is positive, lag is negative | end user
| 0516 | ApparentPower_Load_S | I16 | 0.01 | kVA |  |  | R | SPhase load apparent power. Load consumption is positive and feedback is negative. | end user
| 0517 | LoadPeakRatio_S | U16 | 0.01 | pu |  |  | R | SPhase load peak ratio | end user
| 0518 | Voltage_Load_S | U16 | 0.1 | V |  |  | R | SCorresponding emergency load voltage | end user
| 0519 | ESS_Rsvd2 | [5 empty] | R | SPhase reservation2 | end user
| 051A | Voltage_Output_T | U16 | 0.1 | V |  |  | R | TPhase inverter output voltage | end user
| 051B | Current_Load_T | I16 | 0.01 | A |  |  | R | TPhase load current | end user
| 051C | ActivePower_Load_T | I16 | 0.01 | kW |  |  | R | TPhase load active power. Load consumption is positive and feedback is negative. | end user
| 051D | ReactivePower_Load_T | I16 | 0.01 | kW |  |  | R | TPhase load reactive power. Inverter side lead is positive, lag is negative | end user
| 051E | ApparentPower_Load_T | I16 | 0.01 | kVA |  |  | R | TPhase load apparent power. Load consumption is positive and feedback is negative. | end user
| 051F | LoadPeakRatio_T | U16 | 0.01 | pu |  |  | R | TPhase load peak ratio | end user
| 0520 | Voltage_Load_T | U16 | 0.1 | V |  |  | R | TCorresponding emergency load voltage | end user
| 0521 | EST_Rsvd2 | [5 empty] | R | TPhase reservation2 | end user
| 0522 | Voltage_Output_L1N | U16 | 0.1 | V |  |  | R | InversionL1rightNVoltage RMS | end user
| 0523 | Current_Load_L1N | I16 | 0.01 | A |  |  | R | L1RMS load current | end user
| 0524 | ActivePower_Load_L1N | I16 | 0.01 | kW |  |  | R | loadL1rightNActive power | end user
| 0525 | Voltage_Output_L2N | U16 | 0.1 | V |  |  | R | InversionL2rightNVoltage RMS | end user
| 0526 | Current_Load_L2N | I16 | 0.01 | A |  |  | R | L2RMS load current | end user
| 0527 | ActivePower_Load_L2N | I16 | 0.01 | kW |  |  | R | loadL2rightNActive power | end user
0528
0529
052A
052B
052C
052D
052E
052F
0530
0531
0532
0533
0534
0535
0536
0537
0538
0539
053A
053B
053C
053D
053E
053F
PVenter(0x0580-0x05FF)
| 0580 | AddressMask_Realtime_Input_PV1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0581 | [8 empty] | end user
| 0582 | [8 empty] | end user
| 0583 | [8 empty] | end user
| 0584 | Voltage_PV1 | U16 | 0.1 | V |  |  | R | the first1roadPVVoltage | end user
| 0585 | Current_PV1 | U16 | 0.01 | A |  |  | R | the first1roadPVcurrent | end user
| 0586 | Power_PV1 | U16 | 0.01 | kW |  |  | R | the first1roadPVpower | end user
| 0587 | Voltage_PV2 | U16 | 0.1 | V |  |  | R | the first2 way PV voltage | end user
| 0588 | Current_PV2 | U16 | 0.01 | A |  |  | R | the first2 channels PV current | end user
| 0589 | Power_PV2 | U16 | 0.01 | kW |  |  | R | the first2-way PV power | end user
| 058A | Voltage_PV3 | U16 | 0.1 | V |  |  | R | the first3-way PV voltage | end user
| 058B | Current_PV3 | U16 | 0.01 | A |  |  | R | the first3-way PV current | end user
| 058C | Power_PV3 | U16 | 0.01 | kW |  |  | R | the first3-way PV power | end user
| 058D | Voltage_PV4 | U16 | 0.1 | V |  |  | R | the first4-way PV voltage | end user
| 058E | Current_PV4 | U16 | 0.01 | A |  |  | R | the first4 channels PV current | end user
| 058F | Power_PV4 | U16 | 0.01 | kW |  |  | R | the first4-way PV power | end user
| 0590 | Voltage_PV5 | U16 | 0.1 | V |  |  | R | the first5-way PV voltage | end user
| 0591 | Current_PV5 | U16 | 0.01 | A |  |  | R | the first5-way PV current | end user
| 0592 | Power_PV5 | U16 | 0.01 | kW |  |  | R | the first5-way PV power | end user
| 0593 | Voltage_PV6 | U16 | 0.1 | V |  |  | R | the first6 channels PV voltage | end user
| 0594 | Current_PV6 | U16 | 0.01 | A |  |  | R | the first6 channels PV current | end user
| 0595 | Power_PV6 | U16 | 0.01 | kW |  |  | R | the first6-way PV power | end user
| 0596 | Voltage_PV7 | U16 | 0.1 | V |  |  | R | the first7 channels PV voltage | end user
| 0597 | Current_PV7 | U16 | 0.01 | A |  |  | R | the first7 channels PV current | end user
| 0598 | Power_PV7 | U16 | 0.01 | kW |  |  | R | the first7-way PV power | end user
| 0599 | Voltage_PV8 | U16 | 0.1 | V |  |  | R | the first8 channels PV voltage | end user
| 059A | Current_PV8 | U16 | 0.01 | A |  |  | R | the first8 channels PV current | end user
| 059B | Power_PV8 | U16 | 0.01 | kW |  |  | R | the first8-way PV power | end user
| 059C | Voltage_PV9 | U16 | 0.1 | V |  |  | R | the first9 channels PV voltage | end user
| 059D | Current_PV9 | U16 | 0.01 | A |  |  | R | the first9 channels PV current | end user
| 059E | Power_PV9 | U16 | 0.01 | kW |  |  | R | the first9-way PV power | end user
| 059F | Voltage_PV10 | U16 | 0.1 | V |  |  | R | the first10 channels PV voltage | end user
| 05A0 | Current_PV10 | U16 | 0.01 | A |  |  | R | the first10 channels PV current | end user
| 05A1 | Power_PV10 | U16 | 0.01 | kW |  |  | R | the first10-way PV power | end user
| 05A2 | Voltage_PV11 | U16 | 0.1 | V |  |  | R | the first11 channels PV voltage | end user
| 05A3 | Current_PV11 | U16 | 0.01 | A |  |  | R | the first11 channels PV current | end user
| 05A4 | Power_PV11 | U16 | 0.01 | kW |  |  | R | the first11 channels PV power | end user
| 05A5 | Voltage_PV12 | U16 | 0.1 | V |  |  | R | the first12 channels PV voltage | end user
| 05A6 | Current_PV12 | U16 | 0.01 | A |  |  | R | the first12 channels PV current | end user
| 05A7 | Power_PV12 | U16 | 0.01 | kW |  |  | R | the first12 channels PV power | end user
| 05A8 | Voltage_PV13 | U16 | 0.1 | V |  |  | R | the first13 channels PV voltage | end user
| 05A9 | Current_PV13 | U16 | 0.01 | A |  |  | R | the first13 channels PV current | end user
| 05AA | Power_PV13 | U16 | 0.01 | kW |  |  | R | the first13 channels PV power | end user
| 05AB | Voltage_PV14 | U16 | 0.1 | V |  |  | R | the first14 channels PV voltage | end user
| 05AC | Current_PV14 | U16 | 0.01 | A |  |  | R | the first14 channels PV current | end user
| 05AD | Power_PV14 | U16 | 0.01 | kW |  |  | R | the first14 channels PV power | end user
| 05AE | Voltage_PV15 | U16 | 0.1 | V |  |  | R | the first15 channels PV voltage | end user
| 05AF | Current_PV15 | U16 | 0.01 | A |  |  | R | the first15 channels PV current | end user
| 05B0 | Power_PV15 | U16 | 0.01 | kW |  |  | R | the first15 channels PV power | end user
| 05B1 | Voltage_PV16 | U16 | 0.1 | V |  |  | R | the first16 channels PV voltage | end user
| 05B2 | Current_PV16 | U16 | 0.01 | A |  |  | R | the first16 channels PV current | end user
| 05B3 | Power_PV16 | U16 | 0.01 | kW |  |  | R | the first16 channels PV power | end user
05B4
05B5
05B6
05B7
05B8
05B9
05BA
05BB
05BC
05BD
05BE
05BF
| 05C0 | AddressMask_Realtime_Input_PV2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 05C1 | [8 empty] | end user
| 05C2 | [8 empty] | end user
| 05C3 | [8 empty] | end user
| 05C4 | Power_PV_Total | U16 | 0.1 | kW |  |  | R | totalPVpower | end user
05C5
05C6
05C7
05C8
05C9
05CA
05CB
05CC
05CD
05CE
05CF
05D0
05D1
05D2
05D3
05D4
05D5
05D6
05D7
05D8
05D9
05DA
05DB
05DC
05DD
05DE
05DF
05E0
05E1
05E2
05E3
05E4
05E5
05E6
05E7
05E8
05E9
05EA
05EB
05EC
05ED
05EE
05EF
05F0
05F1
05F2
05F3
Battery input (0x0600-0x067F)
| 0600 | AddressMask_Realtime_Input_Bat1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0601 | [8 empty] | end user
| 0602 | [8 empty] | end user
| 0603 | [8 empty] | end user
| 0604 | Voltage_Bat1 | U16 | 0.1 | V |  |  | R | the first1battery pack voltage | end user
| 0605 | Current_Bat1 | I16 | 0.01 | A |  |  | R | the first1The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 0606 | Power_Bat1 | I16 | 0.01 | kW |  |  | R | the first1battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 0607 | Temperature_Env_Bat1 | I16 | 1 | °C |  |  | R | the first1Road battery pack ambient temperature | end user
| 0608 | SOC_Bat1 | U16 | 1 | % |  |  | R | the first1Road battery packSOC | end user
| 0609 | SOH_Bat1 | U16 | 1 | % |  |  | R | the first1Road battery packSOH | end user
| 060A | ChargeCycle_Bat1 | U16 | 1 | cycle |  |  | R | the first1Battery pack cycle times | end user
| 060B | Voltage_Bat2 | U16 | 0.1 | V |  |  | R | the first2-way battery pack voltage | end user
| 060C | Current_Bat2 | I16 | 0.01 | A |  |  | R | the first2The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 060D | Power_Bat2 | I16 | 0.01 | kW |  |  | R | the first2battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 060E | Temperature_Env_Bat2 | I16 | 1 | °C |  |  | R | the first2-way battery pack ambient temperature | end user
| 060F | SOC_Bat2 | U16 | 1 | % |  |  | R | the first2-way battery pack SOC | end user
| 0610 | SOH_Bat2 | U16 | 1 | % |  |  | R | the first2-way battery pack SOH | end user
| 0611 | ChargeCycle_Bat2 | U16 | 1 | cycle |  |  | R | the first2-way battery pack cycle times | end user
| 0612 | Voltage_Bat3 | U16 | 0.1 | V |  |  | R | the first3-way battery pack voltage | end user
| 0613 | Current_Bat3 | I16 | 0.01 | A |  |  | R | the first3The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 0614 | Power_Bat3 | I16 | 0.01 | kW |  |  | R | the first3battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 0615 | Temperature_Env_Bat3 | I16 | 1 | °C |  |  | R | the first3-way battery pack ambient temperature | end user
| 0616 | SOC_Bat3 | U16 | 1 | % |  |  | R | the first3-way battery pack SOC | end user
| 0617 | SOH_Bat3 | U16 | 1 | % |  |  | R | the first3-way battery pack SOH | end user
| 0618 | ChargeCycle_Bat3 | U16 | 1 | cycle |  |  | R | the first3-way battery pack cycle times | end user
| 0619 | Voltage_Bat4 | U16 | 0.1 | V |  |  | R | the first4-way battery pack voltage | end user
| 061A | Current_Bat4 | I16 | 0.01 | A |  |  | R | the first4The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 061B | Power_Bat4 | I16 | 0.01 | kW |  |  | R | the first4battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 061C | Temperature_Env_Bat4 | I16 | 1 | °C |  |  | R | the first4-way battery pack ambient temperature | end user
| 061D | SOC_Bat4 | U16 | 1 | % |  |  | R | the first4-way battery pack SOC | end user
| 061E | SOH_Bat4 | U16 | 1 | % |  |  | R | the first4-way battery pack SOH | end user
| 061F | ChargeCycle_Bat4 | U16 | 1 | cycle |  |  | R | the first4-way battery pack cycle times | end user
| 0620 | Voltage_Bat5 | U16 | 0.1 | V |  |  | R | the first5-way battery pack voltage | end user
| 0621 | Current_Bat5 | I16 | 0.01 | A |  |  | R | the first5The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 0622 | Power_Bat5 | I16 | 0.01 | kW |  |  | R | the first5battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 0623 | Temperature_Env_Bat5 | I16 | 1 | °C |  |  | R | the first5-way battery pack ambient temperature | end user
| 0624 | SOC_Bat5 | U16 | 1 | % |  |  | R | the first5-way battery pack SOC | end user
| 0625 | SOH_Bat5 | U16 | 1 | % |  |  | R | the first5-way battery pack SOH | end user
| 0626 | ChargeCycle_Bat5 | U16 | 1 | cycle |  |  | R | the first5-way battery pack cycle times | end user
| 0627 | Voltage_Bat6 | U16 | 0.1 | V |  |  | R | the first6-way battery pack voltage | end user
| 0628 | Current_Bat6 | I16 | 0.01 | A |  |  | R | the first6The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 0629 | Power_Bat6 | I16 | 0.01 | kW |  |  | R | the first6battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 062A | Temperature_Env_Bat6 | I16 | 1 | °C |  |  | R | the first6-way battery pack ambient temperature | end user
| 062B | SOC_Bat6 | U16 | 1 | % |  |  | R | the first6-way battery pack SOC | end user
| 062C | SOH_Bat6 | U16 | 1 | % |  |  | R | the first6-way battery pack SOH | end user
| 062D | ChargeCycle_Bat6 | U16 | 1 | cycle |  |  | R | the first6-way battery pack cycle times | end user
| 062E | Voltage_Bat7 | U16 | 0.1 | V |  |  | R | the first7-way battery pack voltage | end user
| 062F | Current_Bat7 | I16 | 0.01 | A |  |  | R | the first7The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 0630 | Power_Bat7 | I16 | 0.01 | kW |  |  | R | the first7battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 0631 | Temperature_Env_Bat7 | I16 | 1 | °C |  |  | R | the first7-way battery pack ambient temperature | end user
| 0632 | SOC_Bat7 | U16 | 1 | % |  |  | R | the first7-way battery pack SOC | end user
| 0633 | SOH_Bat7 | U16 | 1 | % |  |  | R | the first7-way battery pack SOH | end user
| 0634 | ChargeCycle_Bat7 | U16 | 1 | cycle |  |  | R | the first7-way battery pack cycle times | end user
| 0635 | Voltage_Bat8 | U16 | 0.1 | V |  |  | R | the first8-way battery pack voltage | end user
| 0636 | Current_Bat8 | I16 | 0.01 | A |  |  | R | the first8The charging and discharging current of the battery pack. Charge is positive, discharge is negative | end user
| 0637 | Power_Bat8 | I16 | 0.01 | kW |  |  | R | the first8battery pack charging and discharging power. Charge is positive, discharge is negative | end user
| 0638 | Temperature_Env_Bat8 | I16 | 1 | °C |  |  | R | the first8-way battery pack ambient temperature | end user
| 0639 | SOC_Bat8 | U16 | 1 | % |  |  | R | the first8-way battery pack SOC | end user
| 063A | SOH_Bat8 | U16 | 1 | % |  |  | R | the first8-way battery pack SOH | end user
| 063B | ChargeCycle_Bat8 | U16 | 1 | cycle |  |  | R | the first8-way battery pack cycle times | end user
063C
063D
063E
063F
| 0640 | AddressMask_Realtime_Input_Bat2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0641 | [8 empty] | end user
| 0642 | [8 empty] | end user
| 0643 | [8 empty] | end user
| 0644 | Voltage_Bat9 | U16 | 0.1 | V |  |  | R | No. 9 battery pack voltage | end user
| 0645 | Current_Bat9 | I16 | 0.01 | A |  |  | R | No. 9 battery pack charge and discharge current. Charge is positive, discharge is negative | end user
| 0646 | Power_Bat9 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 9th battery pack. Charge is positive, discharge is negative | end user
| 0647 | Temperature_Env_Bat9 | I16 | 1 | °C |  |  | R | The ambient temperature of the 9th battery pack | end user
| 0648 | SOC_Bat9 | U16 | 1 | % |  |  | R | the first9Road battery packSOC | end user
| 0649 | SOH_Bat9 | U16 | 1 | % |  |  | R | the first9Road battery packSOH | end user
| 064A | ChargeCycle_Bat9 | U16 | 1 | cycle |  |  | R | Number of cycles of the 9th battery pack | end user
| 064B | Voltage_Bat10 | U16 | 0.1 | V |  |  | R | No. 10 battery pack voltage | end user
| 064C | Current_Bat10 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the 10th battery pack. Charge is positive, discharge is negative | end user
| 064D | Power_Bat10 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 10th battery pack. Charge is positive, discharge is negative | end user
| 064E | Temperature_Env_Bat10 | I16 | 1 | °C |  |  | R | The ambient temperature of the 10th battery pack | end user
| 064F | SOC_Bat10 | U16 | 1 | % |  |  | R | the first10-way battery pack SOC | end user
| 0650 | SOH_Bat10 | U16 | 1 | % |  |  | R | the first10-way battery pack SOH | end user
| 0651 | ChargeCycle_Bat10 | U16 | 1 | cycle |  |  | R | Number of cycles of the 10th battery pack | end user
| 0652 | Voltage_Bat11 | U16 | 0.1 | V |  |  | R | No. 11 battery pack voltage | end user
| 0653 | Current_Bat11 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the 11th battery pack. Charge is positive, discharge is negative | end user
| 0654 | Power_Bat11 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 11th battery pack. Charge is positive, discharge is negative | end user
| 0655 | Temperature_Env_Bat11 | I16 | 1 | °C |  |  | R | The ambient temperature of the 11th battery pack | end user
| 0656 | SOC_Bat11 | U16 | 1 | % |  |  | R | the first11-way battery pack SOC | end user
| 0657 | SOH_Bat11 | U16 | 1 | % |  |  | R | the first11-way battery pack SOH | end user
| 0658 | ChargeCycle_Bat11 | U16 | 1 | cycle |  |  | R | Cycle times of the 11th battery pack | end user
| 0659 | Voltage_Bat12 | U16 | 0.1 | V |  |  | R | The 12th battery pack voltage | end user
| 065A | Current_Bat12 | I16 | 0.01 | A |  |  | R | The 12th battery pack charge and discharge current. Charge is positive, discharge is negative | end user
| 065B | Power_Bat12 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 12th battery pack. Charge is positive, discharge is negative | end user
| 065C | Temperature_Env_Bat12 | I16 | 1 | °C |  |  | R | The ambient temperature of the 12th battery pack | end user
| 065D | SOC_Bat12 | U16 | 1 | % |  |  | R | the first12-way battery pack SOC | end user
| 065E | SOH_Bat12 | U16 | 1 | % |  |  | R | the first12-way battery pack SOH | end user
| 065F | ChargeCycle_Bat12 | U16 | 1 | cycle |  |  | R | Cycle times of the 12th battery pack | end user
0660
0661
0662
0663
0664
0665
0666
| 0667 | Power_Bat_Total | I16 | 0.1 | kW |  |  | R | Total battery charge and discharge power. Charge is positive, discharge is negative | end user
| 0668 | SOC_Bat_Average | U16 | 1 | % |  |  | R | Aggregate battery packSOCaverage of | end user
| 0669 | SOH_Bat | U16 | 1 | % |  |  | R | Aggregate battery packSOH | end user
| 066A | CurrentBattery_num | U16 | 1 |  |  |  | R | real-time battery
066B
066C
066D
066E
066F
0670
0671
0672
0673
0674
0675
0676
0677
0678
0679
067A
067B
067C
067D
067E
067F
Power (0x0680-0x06BF)
| 0680 | AddressMask_Realtime_ElectricityStatistics1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 0681 | [8 empty] | end user
| 0682 | [8 empty] | end user
| 0683 | [8 empty] | end user
| 0684 | PV_Generation_Today | U32 | 0.01 | kWh |  |  | R | daily power generation | end user
| 0685 | [8 empty] | end user
| 0686 | PV_Generation_Total | U32 | 0.1 | kWh |  |  | R | total power generation | end user
| 0687 | [8 empty] | end user
| 0688 | Load_Consumption_Today | U32 | 0.01 | kWh |  |  | R | Current load power consumption | end user
| 0689 | [8 empty] | end user
| 068A | Load_Consumption_Total | U32 | 0.1 | kWh |  |  | R | Total load power consumption | end user
| 068B | [8 empty] | end user
| 068C | Energy_Purchase_Today | U32 | 0.01 | kWh |  |  | R | Buy electricity on the day | end user
| 068D | [8 empty] | end user
| 068E | Energy_Purchase_Total | U32 | 0.1 | kWh |  |  | R | total electricity purchase | end user
| 068F | [8 empty] | end user
| 0690 | Energy_Selling_Today | U32 | 0.01 | kWh |  |  | R | Electricity sold on the day | end user
| 0691 | [8 empty] | end user
| 0692 | Energy_Selling_Total | U32 | 0.1 | kWh |  |  | R | Total electricity sold | end user
| 0693 | [8 empty] | end user
| 0694 | Bat_Charge_Today | U32 | 0.01 | kWh |  |  | R | Battery charge for the day | end user
| 0695 | [8 empty] | end user
| 0696 | Bat_Charge_Total | U32 | 0.1 | kWh |  |  | R | total battery charge | end user
| 0697 | [8 empty] | end user
| 0698 | Bat_Discharge_Today | U32 | 0.01 | kWh |  |  | R | Battery discharge for the day | end user
| 0699 | [8 empty] | end user
| 069A | Bat_Discharge_Total | U32 | 0.1 | kWh |  |  | R | Total battery discharge | end user
| 069B | [8 empty] | end user
069C
069D
069E
069F
06A0
06A1
06A2
06A3
06A4
06A5
06A6
06A7
06A8
06A9
06AA
06AB
06AC
06AD
06AE
06AF
06B0
06B1
06B2
06B3
06B4
06B5
06B6
06B7
06B8
06B9
06BA
06BB
06BC
06BD
06BE
06BF
Internal information (0x06C0-0x06FF)
| 06C0 | AddressMask_Realtime_ClassifiedInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 06C1 | [8 empty] | installer
| 06C2 | [8 empty] | installer
| 06C3 | [8 empty] | installer
| 06C4 | GFCI | U16 | 1 | mA |  |  | R | leakage current | installer
| 06C5 | Current_Bus_Balance | I16 | 0.01 | A |  |  | R | Balance current | installer
| 06C6 | DCI_R | I16 | 1 | mA |  |  | R | RDC component of phase current | installer
| 06C7 | DCI_S | I16 | 1 | mA |  |  | R | SDC component of phase current | installer
| 06C8 | DCI_T | I16 | 1 | mA |  |  | R | TDC component of phase current | installer
| 06C9 | DCV_R | I16 | 1 | mV |  |  | R | RDC component of phase voltage | installer
| 06CA | DCV_S | I16 | 1 | mV |  |  | R | SDC component of phase voltage | installer
| 06CB | DCV_T | I16 | 1 | mV |  |  | R | TDC component of phase voltage | installer
| 06CC | Voltage_Bus | U16 | 0.1 | V |  |  | R | totalBUSVoltage | installer
| 06CD | Voltage_Bus_P | U16 | 0.1 | V |  |  | R | BUSpositive voltage | installer
| 06CE | Voltage_Bus_N | U16 | 0.1 | V |  |  | R | BUSnegative voltage | installer
| 06CF | Voltage_Bus_LLC | U16 | 0.1 | V |  |  | R | LLC BusVoltage | installer
| 06D0 | Current_BuckBoost | I16 | 0.01 | A |  |  | R | BuckBoostcurrent | installer
| 06D1 | Voltage_Bus_P_Half | U16 | 0.1 | V |  |  | R | BUSPositive half voltage | installer
| 06D2 | Voltage_Bus_N_Half | U16 | 0.1 | V |  |  | R | BUSNegative half voltage | installer
| 06D3 | FlyingCap_Voltage1 | U16 | 0.1 | V |  |  | R | PV1Flying capacitor voltage | installer
| 06D4 | FlyingCap_Voltage2 | U16 | 0.1 | V |  |  | R | PV2 flying capacitor voltage | installer
| 06D5 | FlyingCap_Voltage3 | U16 | 0.1 | V |  |  | R | PV3 flying capacitor voltage | installer
| 06D6 | FlyingCap_Voltage4 | U16 | 0.1 | V |  |  | R | PV4 flying capacitor voltage | installer
| 06D7 | FlyingCap_Voltage5 | U16 | 0.1 | V |  |  | R | PV5 flying capacitor voltage | installer
| 06D8 | FlyingCap_Voltage6 | U16 | 0.1 | V |  |  | R | PV6 flying capacitor voltage | installer
| 06D9 | FlyingCap_Voltage7 | U16 | 0.1 | V |  |  | R | PV7 flying capacitor voltage | installer
| 06DA | FlyingCap_Voltage8 | U16 | 0.1 | V |  |  | R | PV8 flying capacitor voltage | installer
| 06DB | FlyingCap_Voltage9 | U16 | 0.1 | V |  |  | R | PV9 flying capacitor voltage | installer
| 06DC | FlyingCap_Voltage10 | U16 | 0.1 | V |  |  | R | PV10 flying capacitor voltage | installer
| 06DD | FlyingCap_Voltage11 | U16 | 0.1 | V |  |  | R | PV11 flying capacitor voltage | installer
| 06DE | FlyingCap_Voltage12 | U16 | 0.1 | V |  |  | R | PV12 flying capacitor voltage | installer
| 06DF | FlyingCap_Voltage13 | U16 | 0.1 | V |  |  | R | PV13 flying capacitor voltage | installer
| 06E0 | FlyingCap_Voltage14 | U16 | 0.1 | V |  |  | R | PV14 flying capacitor voltage | installer
| 06E1 | FlyingCap_Voltage15 | U16 | 0.1 | V |  |  | R | PV15 flying capacitor voltage | installer
| 06E2 | FlyingCap_Voltage16 | U16 | 0.1 | V |  |  | R | PV16 flying capacitor voltage | installer
| 06E3 | Internal_Info1 | U16 | 0.1 | V |  |  | R | inside information1 | installer
| 06E4 | Internal_Info2 | U16 | 0.1 | V |  |  | R | inside information2 | installer
| 06E5 | Internal_Info3 | U16 | 0.1 | V |  |  | R | inside information3 | installer
| 06E6 | Internal_Info4 | U16 | 0.1 | V |  |  | R | inside information4 | installer
| 06E7 | Internal_Info5 | U16 | 0.1 | V |  |  | R | inside information5 | installer
| 06E8 | Internal_Info6 | U16 | 0.1 | V |  |  | R | inside information6 | installer
| 06E9 | Internal_Info7 | U16 | 0.1 | V |  |  | R | inside information7 | installer
| 06EA | Internal_Info8 | U16 | 0.1 | V |  |  | R | inside information8 | installer
| 06EB | Internal_Info9 | U16 | 0.1 | V |  |  | R | inside information9 | installer
| 06EC | Internal_Info10 | U16 | 0.1 | V |  |  | R | inside information10 | installer
| 06ED | RatedPower_Inverter | U16 | 0.1kW |  |  |  | R | Inverter rated power
06EE
06EF
06F0
06F1
06F2
06F3
06F4
06F5
06F6
06F7
06F8
06F9
06FA
06FB
06FC
06FD
06FE
06FF
Confluence information (0x0700-0x077F)
| 0700 | AddressMask_Realtime_CombinerInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 0701 | [8 empty] | installer
| 0702 | [8 empty] | installer
| 0703 | [8 empty] | installer
| 0704 | Voltage_Group1 | U16 | 0.1 | V |  |  | R | the first1Group bus voltage
| 0705 | Current_Group1_Branch1 | U16 | 0.01 | A |  |  | R | the first1group1String current
| 0706 | Current_Group1_Branch2 | U16 | 0.01 | A |  |  | R | the first1group2-way string current
| 0707 | Voltage_Group2 | U16 | 0.1 | V |  |  | R | the first2 groups of bus voltage
| 0708 | Current_Group2_Branch1 | U16 | 0.01 | A |  |  | R | the first2group1String current
| 0709 | Current_Group2_Branch2 | U16 | 0.01 | A |  |  | R | the first2group2String current
| 070A | Voltage_Group3 | U16 | 0.1 | V |  |  | R | Group 3 bus voltage
| 070B | Current_Group3_Branch1 | U16 | 0.01 | A |  |  | R | the first3group1String current
| 070C | Current_Group3_Branch2 | U16 | 0.01 | A |  |  | R | the first3group2String current
| 070D | Voltage_Group4 | U16 | 0.1 | V |  |  | R | Group 4 bus voltage
| 070E | Current_Group4_Branch1 | U16 | 0.01 | A |  |  | R | the first4group1String current
| 070F | Current_Group4_Branch2 | U16 | 0.01 | A |  |  | R | the first4group2String current
| 0710 | Voltage_Group5 | U16 | 0.1 | V |  |  | R | Group 5 bus voltage
| 0711 | Current_Group5_Branch1 | U16 | 0.01 | A |  |  | R | the first5group1String current
| 0712 | Current_Group5_Branch2 | U16 | 0.01 | A |  |  | R | the first5group2String current
| 0713 | Voltage_Group6 | U16 | 0.1 | V |  |  | R | Group 6 bus voltage
| 0714 | Current_Group6_Branch1 | U16 | 0.01 | A |  |  | R | the first6group1String current
| 0715 | Current_Group6_Branch2 | U16 | 0.01 | A |  |  | R | the first6group2String current
| 0716 | Voltage_Group7 | U16 | 0.1 | V |  |  | R | Group 7 bus voltage
| 0717 | Current_Group7_Branch1 | U16 | 0.01 | A |  |  | R | the first7group1String current
| 0718 | Current_Group7_Branch2 | U16 | 0.01 | A |  |  | R | the first7group2String current
| 0719 | Voltage_Group8 | U16 | 0.1 | V |  |  | R | Group 8 bus voltage
| 071A | Current_Group8_Branch1 | U16 | 0.01 | A |  |  | R | the first8group1String current
| 071B | Current_Group8_Branch2 | U16 | 0.01 | A |  |  | R | the first8group2String current
| 071C | Voltage_Group9 | U16 | 0.1 | V |  |  | R | Group 9 bus voltage
| 071D | Current_Group9_Branch1 | U16 | 0.01 | A |  |  | R | the first9group1String current
| 071E | Current_Group9_Branch2 | U16 | 0.01 | A |  |  | R | the first9group2String current
| 071F | Voltage_Group10 | U16 | 0.1 | V |  |  | R | Group 10 bus voltage
| 0720 | Current_Group10_Branch1 | U16 | 0.01 | A |  |  | R | the first10group1String current
| 0721 | Current_Group10_Branch2 | U16 | 0.01 | A |  |  | R | the first10group2String current
| 0722 | Voltage_Group11 | U16 | 0.1 | V |  |  | R | Group 11 bus voltage
| 0723 | Current_Group11_Branch1 | U16 | 0.01 | A |  |  | R | the first11group1String current
| 0724 | Current_Group11_Branch2 | U16 | 0.01 | A |  |  | R | the first11group2String current
| 0725 | Voltage_Group12 | U16 | 0.1 | V |  |  | R | Group 12 bus voltage
| 0726 | Current_Group12_Branch1 | U16 | 0.01 | A |  |  | R | the first12group1String current
| 0727 | Current_Group12_Branch2 | U16 | 0.01 | A |  |  | R | the first12group2String current
| 0728 | Voltage_Group13 | U16 | 0.1 | V |  |  | R | Group 13 bus voltage
| 0729 | Current_Group13_Branch1 | U16 | 0.01 | A |  |  | R | the first13group1String current
| 072A | Current_Group13_Branch2 | U16 | 0.01 | A |  |  | R | the first13group2String current
| 072B | Voltage_Group14 | U16 | 0.1 | V |  |  | R | Group 14 bus voltage
| 072C | Current_Group14_Branch1 | U16 | 0.01 | A |  |  | R | the first14group1String current
| 072D | Current_Group14_Branch2 | U16 | 0.01 | A |  |  | R | the first14group2String current
| 072E | Voltage_Group15 | U16 | 0.1 | V |  |  | R | Group 15 bus voltage
| 072F | Current_Group15_Branch1 | U16 | 0.01 | A |  |  | R | the first15group1String current
| 0730 | Current_Group15_Branch2 | U16 | 0.01 | A |  |  | R | the first15group2String current
| 0731 | Voltage_Group16 | U16 | 0.1 | V |  |  | R | Group 16 bus voltage
| 0732 | Current_Group16_Branch1 | U16 | 0.01 | A |  |  | R | the first16group1String current
| 0733 | Current_Group16_Branch2 | U16 | 0.01 | A |  |  | R | the first16group2String current
0734
0735
0736
0737
0738
0739
073A
073B
073C
073D
073E
073F
| 0740 | AddressMask_Realtime_CombinerInfo2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 0741 | [8 empty] | installer
| 0742 | [8 empty] | installer
| 0743 | [8 empty] | installer
| 0744 | Current_Group1_Branch3 | U16 | 0.01 | A |  |  | R | the first1group3String current
| 0745 | Current_Group1_Branch4 | U16 | 0.01 | A |  |  | R | the first1Group No. 4 string current
| 0746 | Current_Group2_Branch3 | U16 | 0.01 | A |  |  | R | Group 23String current
| 0747 | Current_Group2_Branch4 | U16 | 0.01 | A |  |  | R | Group 2 and No. 4 string current
| 0748 | Current_Group3_Branch3 | U16 | 0.01 | A |  |  | R | Group 33String current
| 0749 | Current_Group3_Branch4 | U16 | 0.01 | A |  |  | R | The third group and the fourth string current
| 074A | Current_Group4_Branch3 | U16 | 0.01 | A |  |  | R | Group 43String current
| 074B | Current_Group4_Branch4 | U16 | 0.01 | A |  |  | R | 4th group 4th string current
| 074C | Current_Group5_Branch3 | U16 | 0.01 | A |  |  | R | Group 53String current
| 074D | Current_Group5_Branch4 | U16 | 0.01 | A |  |  | R | Group 5, No. 4 string current
| 074E | Current_Group6_Branch3 | U16 | 0.01 | A |  |  | R | Group 63String current
| 074F | Current_Group6_Branch4 | U16 | 0.01 | A |  |  | R | The 6th group 4th string current
| 0750 | Current_Group7_Branch3 | U16 | 0.01 | A |  |  | R | Group 73String current
| 0751 | Current_Group7_Branch4 | U16 | 0.01 | A |  |  | R | The 7th group 4th string current
| 0752 | Current_Group8_Branch3 | U16 | 0.01 | A |  |  | R | Group 83String current
| 0753 | Current_Group8_Branch4 | U16 | 0.01 | A |  |  | R | The 8th group 4th string current
| 0754 | Current_Group9_Branch3 | U16 | 0.01 | A |  |  | R | Group 93String current
| 0755 | Current_Group9_Branch4 | U16 | 0.01 | A |  |  | R | The 9th group 4th string current
| 0756 | Current_Group10_Branch3 | U16 | 0.01 | A |  |  | R | Group 103String current
| 0757 | Current_Group10_Branch4 | U16 | 0.01 | A |  |  | R | Group 10, No. 4 string current
| 0758 | Current_Group11_Branch3 | U16 | 0.01 | A |  |  | R | 1st1group3String current
| 0759 | Current_Group11_Branch4 | U16 | 0.01 | A |  |  | R | 1st1Group No. 4 string current
| 075A | Current_Group12_Branch3 | U16 | 0.01 | A |  |  | R | group 123String current
| 075B | Current_Group12_Branch4 | U16 | 0.01 | A |  |  | R | The 12th group 4th string current
| 075C | Current_Group13_Branch3 | U16 | 0.01 | A |  |  | R | Group 133String current
| 075D | Current_Group13_Branch4 | U16 | 0.01 | A |  |  | R | The 13th group 4th string current
| 075E | Current_Group14_Branch3 | U16 | 0.01 | A |  |  | R | group 143String current
| 075F | Current_Group14_Branch4 | U16 | 0.01 | A |  |  | R | Group 14, No. 4 string current
| 0760 | Current_Group15_Branch3 | U16 | 0.01 | A |  |  | R | group 153String current
| 0761 | Current_Group15_Branch4 | U16 | 0.01 | A |  |  | R | Group 15, No. 4 string current
| 0762 | Current_Group16_Branch3 | U16 | 0.01 | A |  |  | R | Group 163String current
| 0763 | Current_Group16_Branch4 | U16 | 0.01 | A |  |  | R | Group 16, No. 4 string current
0764
0765
0766
0767
0768
0769
076A
076B
076C
076D
076E
076F
0770
0771
0772
0773
0774
0775
0776
0777
0778
0779
077A
077B
077C
077D
077E
077F
Arc information (0x0780-0x07C8)
| 0780 | AddressMask_Realtime_ArcInfo3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 0781 | [8 empty] | installer
| 0782 | [8 empty] | installer
| 0783 | [8 empty] | installer
| 0784 | ArcStrength_MPPT_1 | I16 | 1 |  |  |  | R | MPPT 1Monitored real-time arc strength
| 0785 | ArcStrength_MPPT_2 | I16 | 1 |  |  |  | R | MPPT 2Monitored real-time arc strength
| 0786 | ArcStrength_MPPT_3 | I16 | 1 |  |  |  | R | MPPT 3Monitored real-time arc strength
| 0787 | ArcStrength_MPPT_4 | I16 | 1 |  |  |  | R | MPPT 4Monitored real-time arc strength
| 0788 | ArcStrength_MPPT_5 | I16 | 1 |  |  |  | R | MPPT 5Monitored real-time arc strength
| 0789 | ArcStrength_MPPT_6 | I16 | 1 |  |  |  | R | MPPT 6Monitored real-time arc strength
| 078A | ArcStrength_MPPT_7 | I16 | 1 |  |  |  | R | MPPT 7Monitored real-time arc strength
| 078B | ArcStrength_MPPT_8 | I16 | 1 |  |  |  | R | MPPT 8Monitored real-time arc strength
| 078C | ArcStrength_MPPT_9 | I16 | 1 |  |  |  | R | MPPT 9Monitored real-time arc strength
| 078D | ArcStrength_MPPT_10 | I16 | 1 |  |  |  | R | MPPT 10 Monitored real-time arc strength
| 078E | ArcStrength_MPPT_11 | I16 | 1 |  |  |  | R | MPPT 11 Monitored real-time arc strength
| 078F | ArcStrength_MPPT_12 | I16 | 1 |  |  |  | R | MPPT 12 Monitored real-time arc strength
| 0790 | ArcStrength_MPPT_13 | I16 | 1 |  |  |  | R | MPPT 13 Monitored real-time arc strength
| 0791 | ArcStrength_MPPT_14 | I16 | 1 |  |  |  | R | MPPT 14 Monitored real-time arc strength
| 0792 | ArcStrength_MPPT_15 | I16 | 1 |  |  |  | R | MPPT 15 Monitored real-time arc strength
| 0793 | ArcStrength_MPPT_16 | I16 | 1 |  |  |  | R | MPPT 16 Monitored real-time arc strength
| 0794 | ArcStrength_MPPT_17 | I16 | 1 |  |  |  | R | MPPT 17 Monitored real-time arc strength
| 0795 | ArcStrength_MPPT_18 | I16 | 1 |  |  |  | R | MPPT 18 Monitored real-time arc strength
| 0796 | ArcStrength_MPPT_19 | I16 | 1 |  |  |  | R | MPPT 19 Monitored real-time arc strength
| 0797 | ArcStrength_MPPT_20 | I16 | 1 |  |  |  | R | MPPT 20 Monitored real-time arc strength
| 0798 | ArcStrength_MPPT_21 | I16 | 1 |  |  |  | R | MPPT 21 Monitored real-time arc strength
| 0799 | ArcStrength_MPPT_22 | I16 | 1 |  |  |  | R | MPPT 22 Monitored real-time arc strength
| 079A | ArcStrength_MPPT_23 | I16 | 1 |  |  |  | R | MPPT 23 Monitored real-time arc strength
| 079B | ArcStrength_MPPT_24 | I16 | 1 |  |  |  | R | MPPT 24Monitored real-time arc strength
| 079C |  | I16 | 1 |  |  |  | R
| 079D |  | I16 | 1 |  |  |  | R
| 079E |  | I16 | 1 |  |  |  | R
| 079F |  | I16 | 1 |  |  |  | R
| 07A0 |  | I16 | 1 |  |  |  | R
| 07A1 |  | I16 | 1 |  |  |  | R
| 07A2 | ArcStrength_history_Channel1 | I16 | 1 |  |  |  | R | After channel 1 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off
| 07A3 | ArcStrength_history_Channel2 | I16 | 1 |  |  |  | R | After channel 2 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear after power off
| 07A4 | ArcStrength_history_Channel3 | I16 | 1 |  |  |  | R | After the channel 3 is powered on, record the historical maximum value of the arc intensity monitored, and it will be automatically cleared after power off.
| 07A5 | ArcStrength_history_Channel4 | I16 | 1 |  |  |  | R | Channel 4 records the historical maximum value of arc intensity monitored after power-on, and clears it automatically after power-off
| 07A6 | ArcStrength_history_Channel5 | I16 | 1 |  |  |  | R | After channel 5 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear after power off
| 07A7 | ArcStrength_history_Channel6 | I16 | 1 |  |  |  | R | After channel 6 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear it after power off
| 07A8 | ArcStrength_history_Channel7 | I16 | 1 |  |  |  | R | After channel 7 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear it after power off
| 07A9 | ArcStrength_history_Channel8 | I16 | 1 |  |  |  | R | After channel 8 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear it after power off
| 07AA | ArcStrength_history_Channel9 | I16 | 1 |  |  |  | R | After channel 9 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear after power off
| 07AB | ArcStrength_history_Channel10 | I16 | 1 |  |  |  | R | After channel 10 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear it after power off
| 07AC | ArcStrength_history_Channel11 | I16 | 1 |  |  |  | R | After the channel 11 is powered on, record the historical maximum value of the arc intensity monitored, and it will be automatically cleared after power off.
| 07AD | ArcStrength_history_Channel12 | I16 | 1 |  |  |  | R | After the channel 12 is powered on, record the historical maximum value of the arc intensity monitored, and it will be automatically cleared after power off.
| 07AE | ArcStrength_history_Channel13 | I16 | 1 |  |  |  | R | After channel 13 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off
| 07AF | ArcStrength_history_Channel14 | I16 | 1 |  |  |  | R | After channel 14 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear after power off
| 07B0 | ArcStrength_history_Channel15 | I16 | 1 |  |  |  | R | After the channel 15 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off.
| 07B1 | ArcStrength_history_Channel16 | I16 | 1 |  |  |  | R | After the channel 16 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off.
| 07B2 | ArcStrength_history_Channel17 | I16 | 1 |  |  |  | R | After channel 17 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off
| 07B3 | ArcStrength_history_Channel18 | I16 | 1 |  |  |  | R | After the channel 18 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off.
| 07B4 | ArcStrength_history_Channel19 | I16 | 1 |  |  |  | R | After the channel 19 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off.
| 07B5 | ArcStrength_history_Channel20 | I16 | 1 |  |  |  | R | After channel 20 is powered on, record the historical maximum value of arc intensity monitored, and automatically clear it after power off
| 07B6 | ArcStrength_history_Channel21 | I16 | 1 |  |  |  | R | After the channel 21 is powered on, record the historical maximum value of the arc intensity monitored, and it will be automatically cleared after power off.
| 07B7 | ArcStrength_history_Channel22 | I16 | 1 |  |  |  | R | After the channel 22 is powered on, record the historical maximum value of the arc intensity monitored, and it will be automatically cleared after power off.
| 07B8 | ArcStrength_history_Channel23 | I16 | 1 |  |  |  | R | After channel 23 is powered on, record the historical maximum value of arc intensity monitored, and it will be automatically cleared after power off
| 07B9 | ArcStrength_history_Channel24 | I16 | 1 |  |  |  | R | After the channel 24 is powered on, record the historical maximum value of the arc intensity monitored, and it will be automatically cleared after power off.
| 07BA |  | I16 | 1 |  |  |  | R
| 07BB |  | I16 | 1 |  |  |  | R
| 07BC |  | I16 | 1 |  |  |  | R
| 07BD |  | I16 | 1 |  |  |  | R
| 07BE |  | I16 | 1 |  |  |  | R
| 07BF |  | I16 | 1 |  |  |  | R
| 07C0 | AddressMask_Realtime_ArcInfo4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 07C1 | [8 empty] | installer
| 07C2 | [8 empty] | installer
| 07C3 | [8 empty] | installer
| 07C4 | arc_peak_to_peak | U16 | 1 |  |  |  | R | Arc maximum peak-to-peak value
| 07C5 | arc_variance | U16 | 1 |  |  |  | R | arc maximum variance
| 07C6 | arc_harmonic_energy | U16 | 1 |  |  |  | R | arc maximum harmonic energy
| 07C7 | arc_amplitude_variance | U16 | 1 |  |  |  | R | Arc maximum amplitude variance
07C8
Safety parameter area (0x0800-0x0FFF)
Boot parameters (0x0800-0x083F)
| 0800 | ConnectWaitTime | U16 | 1 | second | 1 | 65535 | RW | Waiting time before grid connection | installer
| 0801 | PowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100express1The rate corresponding to the full load in minutes, and other values are multiplied and divided based on this | installer
| 0802 | ReconnectWaitTime | U16 | 1 | second | 1 | 65535 | RW | Waiting time before reconnecting to the grid after grid fault recovery | installer
| 0803 | ReconnectPowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100express1The rate corresponding to the full load in minutes, and other values are multiplied and divided based on this | installer
| 0804 | VoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | Start grid voltage upper limit | end user
| 0805 | VoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | Start grid voltage lower limit | end user
| 0806 | FreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Start grid frequency cap | end user
| 0807 | FreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Start grid frequency lower limit | end user
| 0808 | ReconnectVoltHighLimit | U16 | 0.1 | V | 0 | 65535 | RW | Reconnection grid voltage upper limit | end user
| 0809 | ReconnectVoltLowLimit | U16 | 0.1 | V | 0 | 65535 | RW | Reconnection grid voltage lower limit | end user
| 080A | ReconnectFreqHighLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Reconnection grid frequency upper limit | end user
| 080B | ReconnectFreqLowLimit | U16 | 0.01 | Hz | 4000 | 7000 | RW | Reconnection grid frequency lower limit | end user
| 0801 | PowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100express1The rate corresponding to the full load in minutes, and other values are multiplied and divided based on this
| 0803 | ReconnectPowerUpSpeed | U16 | 1 | %Pn/min | 1 | 3000 | RW | 100express1The rate corresponding to the full load in minutes, and other values are multiplied and divided based on this
Voltage protection parameters (0x0840-0x087F)
| 0840 | Voltage Config | U16 |  |  |  |  | RW | Bit0 : Overvoltage primary protection enable bitBit1 : Overvoltage secondary protection enable bitBit2 : Overvoltage three-level protection enable bitBit3 Undervoltage primary protection enable bitBit4 : Undervoltage secondary protection enable bitBit5 : Undervoltage three-level protection enable bitBit6:10Minute overvoltage protection enable bit | installer
| 0841 | RatedVoltage | U16 | 0.1 | V | 0 | 65535 | RW | Rated grid voltage | installer
| 0842 | FirstOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Level 1 overvoltage protection value | end user
| 0843 | FirstOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Level 1 overvoltage protection time | installer
| 0844 | SecondOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Secondary overvoltage protection value | end user
| 0845 | SecondOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Secondary overvoltage protection time | installer
| 0846 | ThirdOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Three-level overvoltage protection value | end user
| 0847 | ThirdOvervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Three-level overvoltage protection time | installer
| 0848 | FirstUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Level 1 undervoltage protection value | end user
| 0849 | FirstUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Level 1 undervoltage protection time | installer
| 084A | SecondUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Secondary undervoltage protection value | end user
| 084B | SecondUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Secondary undervoltage protection time | installer
| 084C | ThirdUnderVoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | Three-level undervoltage protection value | end user
| 084D | ThirdUndervoltageProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Three-level undervoltage protection time | installer
| 084E | 10MinOvervoltageProtectionValue | U16 | 0.1 | V | 0 | 65535 | RW | grid10Minute overvoltage protection value | installer
| 084F | FirstOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | Level 1 overvoltage protection time high | installer
| 0850 | SecondOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | Secondary overvoltage protection time high | installer
| 0851 | ThirdOvervoltageProtectionTimeHi | U16 |  |  | 0 | 255 | RW | Level 3 overvoltage protection time high | installer
Frequency protection parameters (0x0880-0x08BF)
| 0880 | FrequencyConfig | U16 |  |  |  |  | RW | Bit0 Overfrequency primary protection enable bit Bit1 Overfrequency secondary protection enable bit Bit2 Overfrequency three-level protection enable bit Bit3 Underfrequency primary protection enable bit Bit4 Underfrequency secondary protection enable bit Bit5Underfrequency three-level protection enable bit | installer
| 0881 | RatedFrequency | U16 | 0.01 | Hz | 4000 | 7000 | RW | Rated grid frequency | installer
| 0882 | FirstOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | Level 1 overfrequency protection value | end user
| 0883 | FirstOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Level 1 overfrequency protection time | installer
| 0884 | SecondOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | Secondary overfrequency protection value | end user
| 0885 | SecondOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Secondary overfrequency protection time | installer
| 0886 | ThirdOverfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | Level 3 overfrequency protection value | end user
| 0887 | ThirdOverfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Three-level overfrequency protection time | installer
| 0888 | FirstUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | Level 1 underfrequency protection value | end user
| 0889 | FirstUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Level 1 underfrequency protection time | installer
| 088A | SecondUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | Secondary underfrequency protection value | end user
| 088B | SecondUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Secondary underfrequency protection time | installer
| 088C | ThirdUnderfrequencyProtectionValue | U16 | 0.01 | Hz | 4000 | 7000 | RW | Three-level underfrequency protection value | end user
| 088D | ThirdUnderfrequencyProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | Three-level underfrequency protection time | installer
DCIProtection parameters(0x08C0-0x08FF)
| 08C0 | DCI Config | U16 |  |  |  |  | RW | Bit0: DCIPrimary protection enable bitBit1: DCI Secondary protection enable bitBit2: DCI Three-level protection enable bitBit3: DCItest enable bit | installer
| 08C1 | DCIFirstProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCIPrimary protection value | installer
| 08C2 | DCIFirstProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCIPrimary protection time | installer
| 08C3 | DCISecondProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCISecondary protection value | installer
| 08C4 | DCISecondProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCISecondary protection time | installer
| 08C5 | DCIThirdProtectionValue | U16 | 1 | mA | 1 | 65535 | RW | DCItertiary protection value | installer
| 08C6 | DCIThirdProtectionTime | U16 | 10 | ms | 1 | 65535 | RW | DCILevel 3 protection time | installer
| 08C7 | DCITestValue1 | I16 | 1 | mA | -32768 | 32767 | RW | DCI RPhase test value | installer
| 08C8 | DCITestValue2 | I16 | 1 | mA | -32768 | 32767 | RW | DCI SPhase test value | installer
| 08C9 | DCITestValue3 | I16 | 1 | mA | -32768 | 32767 | RW | DCITPhase test value | installer
| 08CA | DCIFirstProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCIPrimary protection ratio | installer
| 08CB | DCISecondProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCISecondary protection ratio | installer
| 08CC | DCIThirdProtectionProportion | U16 | 0.01 | % | 1 | 65535 | RW | DCIThree-level protection ratio | installer
Active power, overvoltage and undervoltage drop load parameters (0x0900-0x093F)
| 0900 | Remote Config | U16 |  |  |  |  | RW | Bit0 : Active load shedding enable bitBit1 : Remote switch enable bitBit2 : Overvoltage drop load enable bitBit3 : Overvoltage charge droopBit4 : Undervoltage drop charging power enable bitBit5:DRM0 enable bitBit6: logical interface (DRM1-8 ) enable bitBit7: Anti-reverse current overload enable bit Bit8: Voltage drop loadPTCurve enable bit | installer
| 0901 | ActiveOutputLimit | U16 | 0.1 | % | 0 | 1000 | RW | Active output percentage | installer
| 0902 | ActiveOutputDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | Active load shedding rate
| 0903 | GridVoltageDropStart | U16 | 0.1 | V | 0 | 65535 | RW | Grid overvoltage drop load starting point | installer
| 0904 | GridVoltageDropStop | U16 | 0.1 | V | 0 | 65535 | RW | Grid overvoltage drop load termination point | installer
| 0905 | GridVoltageDropMinPower | I16 | 1 | % | -100 | 100 | RW | Power grid overvoltage drop load cut-off power | installer
| 0906 | OvervoltageDownSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | Overvoltage drop rate | installer
| 0907 | ChgDerateVoltStart | U16 | 0.1 | V | 0 | 65535 | RW | Grid undervoltage drop load starting point | installer
| 0908 | ChgDerateVoltEnd | U16 | 0.1 | V | 0 | 65535 | RW | Power grid undervoltage drop load termination point | installer
| 0909 | ChgDerateMinPower | I16 | 1 | % | -100 | 100 | RW | Power grid undervoltage drop load cut-off power | installer
| 090A | PowerForLogic1 | I16 | 1 | % | -100 | 100 | RW | logical interface1Corresponding power | installer
| 090B | PowerForLogic2 | I16 | 1 | % | -100 | 100 | RW | logical interface2Corresponding power | installer
| 090C | PowerForLogic3 | I16 | 1 | % | -100 | 100 | RW | logical interface3Corresponding power | installer
| 090D | PowerForLogic4 | I16 | 1 | % | -100 | 100 | RW | logical interface4Corresponding power | installer
| 090E | PowerForLogic5 | I16 | 1 | % | -100 | 100 | RW | logical interface5Corresponding power | installer
| 090F | PowerForLogic6 | I16 | 1 | % | -100 | 100 | RW | logical interface6Corresponding power | installer
| 0910 | PowerForLogic7 | I16 | 1 | % | -100 | 100 | RW | logical interface7Corresponding power | installer
| 0911 | PowerForLogic8 | I16 | 1 | % | -100 | 100 | RW | logical interface8Corresponding power | installer
| 0912 | RefluxPower | U16 | 1 | % | 0 | 100 | RW | Anti-reverse current power (VDE4105 safety regulation grid-connected power upper limit) | installer
| 0913 | RefluxOVloadTime | U16 | 10 | ms | 0 | 65535 | RW | Anti-reverse current overload time (VDE4105 safety regulation reverse current overload off-grid time) | installer
| 0914 | LogicDerateSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | Logical interface load shedding rate | installer
| 0915 | LogicReloadSpeed | U16 | 1 | %Pn/min | 1 | 65535 | RW | Logical interface loopback rate | installer
| 0916 | VoltageDerateResponseTime | U16 | 1 | second | 0 | 65535 | RW | Voltage drop time | installer
Overfrequency and underfrequency load reduction parameters (0x0940-0x097F)
| 0940 | FrequencyDerateConfig | U16 |  |  |  |  | RW | Bit0 : Overfrequency output load reduction enableBit1 : Underfrequency input load shedding enableBit2 : Overfrequency Load Back EnableBit3 : Underfrequency load back enableBit4 : Enable load reduction from rated powerBit5: Current power calculation load shedding slope enable Bit6: Energy storage segment curve enable Bit7 : maximum power calculation enableBit12-13: load shedding mode (0Slope Mode/1frequency range mode) | installer
| 0941 | OverfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | Overfrequency load reduction starting frequency | installer
| 0942 | OverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | Overfrequency underload cutoff frequency. Frequency range mode active | installer
| 0943 | OverfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | Overfrequency load shedding slope percentage. Slope mode valid German standard slope=1/(s*fn) | installer
| 0944 | OverfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | Overfrequency load reduction start waiting time | installer
| 0945 | OverfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | Waiting time before overloading | installer
| 0946 | OverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | Overfrequency reduces the load-return frequency. It takes effect when over-frequency backload is prohibited. | installer
| 0947 | OverfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | Overfrequency loopback rate percentage | installer
| 0948 | UnderfrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | Underfrequency load reduction starting frequency | installer
| 0949 | UnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | Underfrequency cut-off frequency for load reduction. Frequency range mode active | installer
| 094A | UnderfrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | Underfrequency load shedding slope percentage. Slope mode active | installer
| 094B | UnderfrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | Under-frequency load reduction start waiting time | installer
| 094C | UnderfrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | Waiting time before underfrequency load back | installer
| 094D | UnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | Under-frequency load-reduction and load-return frequency. It takes effect when underfrequency loadback is prohibited. | installer
| 094E | UnderfrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | Underfrequency loadback rate percentage | installer
| 094F | FrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | Exit to derate the maximum frequency. Over and under frequency sharing. It takes effect when over-frequency loadback is allowed | installer
| 0950 | FrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | Exit load reduction minimum frequency. Over and under frequency sharing. It takes effect when underfrequency loadback is allowed | installer
| 0951 | ESSOverFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency load reduction starting frequency | installer
| 0952 | ESSOverfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Cut-off frequency for over-frequency load reduction. Frequency range mode active
| 0953 | ESSOverFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy storage) The percentage of over-frequency load shedding slope. Slope mode valid German standard slope=1/(s*fn) | installer
| 0954 | ESSOverFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Waiting time for over-frequency load reduction to start | installer
| 0955 | ESSOverFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Waiting time before overloading | installer
| 0956 | ESSOverfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency and load-reduction frequency. It takes effect when over-frequency backload is prohibited. | installer
| 0957 | ESSOverFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | (Energy storage) percentage of overfrequency reload rate | installer
| 0958 | ESSUnderFrequencyStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency load reduction starting frequency | installer
| 0959 | ESSUnderfrequencyEnd | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Cut-off frequency of under-frequency load reduction. Frequency range mode active
| 095A | ESSUnderFrequencySlope | U16 | 1 | %Pn/Hz | 1 | 300 | RW | (Energy storage) Underfrequency load shedding slope percentage. Slope mode active | installer
| 095B | ESSUnderFrequencyResponseDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Waiting time for under-frequency load reduction to start | installer
| 095C | ESSUnderFrequencyReloadDelay | U16 | 10 | ms | 0 | 65535 | RW | (Energy storage) Waiting time before underfrequency load back | installer
| 095D | ESSUnderfrequencyReloadStart | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Under-frequency load-reduction and load-return frequency. It takes effect when underfrequency loadback is prohibited. | installer
| 095E | ESSUnderFrequencyReloadSpeed | U16 | 1 | %Pn/min | 1 | 300 | RW | (Energy storage) Under-frequency load-back rate percentage | installer
| 095F | ESSFrequencyRecoverMax | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Exit the maximum frequency of derating. Over and under frequency sharing | installer
| 0960 | ESSFrequencyRecoverMin | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Exit the minimum frequency of load reduction. Over and under frequency sharing | installer
| 0961 | ESSOverFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) Over-frequency and load-reducing power cross frequency point. Valid when 0940 Bit6 is enabled. | installer
| 0962 | ESSUnderFrequencyTransition | U16 | 0.01 | Hz | 4000 | 7000 | RW | (Energy storage) The under-frequency load-reducing power crosses the frequency point. Valid when 0940 Bit6 is enabled. | installer
Reactive power parameters (0x0980-0x09BF)
| 0980 | ReactiveConfig | U16 |  |  |  |  | RW | Bit0 : reactive enableBit1-3 : reactive modeBit8: Reactive mode three voltage entry enable bit Bit9: Charging reactive enable Bit10: Reactive mode four Austrian enable bit | installer
| 0981 | PowerFactor | I16 | 0.0001 |  | -10000 | 10000 | RW | Power factor, for reactive mode one calculationTanphi. A positive value means providing inductive under-excitation reactive power, and the inverter output current leads the grid voltage; a negative value means providing capacitive over-excitation reactive power, and the inverter output current lags the grid voltage; | installer
| 0982 | FixedReactivePercentage | I16 | 0.01 | % | -6000 | 6000 | RW | The percentage of fixed reactive power is used to calculate reactive power in reactive power mode 2. A positive value means providing inductive under-excitation reactive power, and the inverter output current leads the grid voltage; a negative value means providing capacitive over-excitation reactive power, and the inverter output current lags the grid voltage; | installer
| 0983 | ReactiveCos1 | I16 | 0.0001 |  | -10000 | 10000 | RW | Used for reactive power mode three, the first point power factor value. A positive value means providing inductive under-excitation reactive power, and the inverter output current leads the grid voltage; a negative value means providing capacitive over-excitation reactive power, and the inverter output current lags the grid voltage; | installer
| 0984 | ReactivedynamicValue1 | I16 | 1 | % | -100 | 100 | RW | For reactive mode three, the first point power percentage | installer
| 0985 | ReactiveCos2 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode three, the second point power factor value | installer
| 0986 | ReactivedynamicValue2 | I16 | 1 | % | -100 | 100 | RW | For reactive mode three, the second point power percentage | installer
| 0987 | ReactiveCos3 | I16 | 0.0001 |  | -10000 | 10000 | RW | Used for reactive mode three, the third point power factor value | installer
| 0988 | ReactivedynamicValue3 | I16 | 1 | % | -100 | 100 | RW | For reactive mode three, the third point power percentage | installer
| 0989 | ReactiveCos4 | I16 | 0.0001 |  | -10000 | 10000 | RW | For reactive mode three, the fourth point power factor value | installer
| 098A | ReactivedynamicValue4 | I16 | 1 | % | -100 | 100 | RW | Used for reactive mode three, the fourth point power percentage | installer
| 098B | LockinV | U16 | 1 | % | 0 | 200 | RW | For reactive mode three,LockinVVoltage value percentage | installer
| 098C | LockoutV | U16 | 1 | % | 0 | 200 | RW | For reactive mode three,LockoutVVoltage value percentage | installer
| 098D | HighVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode four, the percentage of high voltage starting voltage | installer
| 098E | HighVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode four, high voltage termination voltage percentage | installer
| 098F | LowVoltStartValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode four, low voltage starting voltage percentage | installer
| 0990 | LowVoltEndValue4 | U16 | 1 | % | 0 | 200 | RW | For reactive mode four, low voltage termination voltage percentage | installer
| 0991 | LockinPower4 | U16 | 1 | % | 0 | 100 | RW | For reactive mode four,LockinPower value percentage | installer
| 0992 | LockoutPower4 | U16 | 1 | % | 0 | 100 | RW | For reactive mode four,LockoutPower value percentage | installer
| 0993 | MaxLeadingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | Used in reactive mode four, the maximum leading reactive power percentage | installer
| 0994 | ReactiveResponseWaitTime4 | U16 | 10 | ms | 0 | 65535 | RW | For reactive mode four, reactive response waiting time | installer
| 0995 | ReactivePowerOffset4 | I16 | 0.01 | %Qmax | -10000 | 10000 | RW | For reactive mode four, reactive power offset percentage. Offsets the reactive power curve over the entire operating voltage range. Positive values are leading, negative values are lagging. | installer
| 0996 | ReactivePowerStart4 | U16 | 0.01 | %Pn | -10000 | 10000 | RW | Used for reactive power mode 4, 50% of the reactive power variation range from the low voltage starting voltage to the high voltage starting voltage point. The low-voltage starting voltage corresponds to the reactive power lagging behind the register; the high-voltage starting voltage corresponds to the reactive power leading the register; | installer
| 0997 | HighVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode five, the percentage of high voltage starting voltage | installer
| 0998 | HighVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode five, high voltage termination voltage percentage | installer
| 0999 | LowVoltStartValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode five, low voltage starting voltage percentage | installer
| 099A | LowVoltEndValue5 | U16 | 1 | % | 0 | 200 | RW | For reactive mode five, low voltage termination voltage percentage | installer
| 099B | LockinPower5 | U16 | 1 | % | 0 | 100 | RW | For reactive mode five,LockinPower value percentage | installer
| 099C | LockoutPower5 | U16 | 1 | % | 0 | 100 | RW | For reactive mode five,LockoutPower value percentage | installer
| 099D | MaxReactivePower5 | U16 | 0.01 | % | 0 | 10000 | RW | Used in reactive mode five, maximum reactive power percentage | installer
| 099E | ReactiveResponseWaitTime5 | U16 | 10 | ms | 0 | 65535 | RW | Used for reactive power mode five, reactive power response waiting time | installer
| 099F | PhaseType | U16 |  |  | 0 | 2 | RW | For reactive mode six, phase type 0: zero reactive power 1: lagging reactive power 2: leading reactive power | installer
| 09A0 | ReactiveResponsePeriod | U16 | 1 | second | 1 | 65535 | RW | for reactive (1,2,3,4,5,6) to set the duration of reactive power adjustment | installer
| 09A1 | MaxLaggingReactivePower4 | U16 | 0.01 | %Pn | 0 | 10000 | RW | Reactive mode 4, the maximum hysteresis reactive power percentage | installer
09A2
09A3
09A4
09A5
09A6
09A7
09A8
09A9
Voltage ride through parameters (0x09C0-0x09FF)
| 09C0 | VRTConfig | U16 |  |  |  |  | RW | Bit0:LVRT enable bitBit1:OVRT enable bitBit2 : Zero current mode enable bitBit3: Inherit the reactive current before passing through Bit4: Calculate the current using the voltage before the drop Bit5: Negative sequence current enable bit Bit6 : High wear active enable bitBit8-11Voltage ride-through current calculation mode | installer
| 09C1 | LvrtInVolt | U16 | 1 | % | 0 | 65535 | RW | EnterLVRTVoltage value percentage | installer
| 09C2 | LvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | Low voltage ride through first point voltage percentage | installer
| 09C3 | LvrtFirstPointTime | U16 | 1 | ms | 0 | 65535 | RW | Low pressure crossing first time | installer
| 09C4 | LvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | Low Voltage Ride Through Second Point Voltage Percentage | installer
| 09C5 | LvrtSecondPointTime | U16 | 1 | ms | 0 | 65535 | RW | Low pressure crossing second point time | installer
| 09C6 | LvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | Low voltage ride through third point voltage percentage | installer
| 09C7 | LvrtThirdPointTime | U16 | 1 | ms | 0 | 65535 | RW | Low pressure crossing third time | installer
| 09C8 | LvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | Low voltage ride through fourth point voltage percentage | installer
| 09C9 | LvrtFourthPointTime | U16 | 1 | ms | 0 | 65535 | RW | Low pressure crossing fourth time | installer
| 09CA | LvrtReactiveCurrentCoefficientK | U16 | 0.1 | pu | 0 | 65535 | RW | Low voltage ride through reactive current coefficientK | installer
| 09CB | LvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after low pressure ride through recovery | installer
| 09CC | LvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | Low Voltage Ride Through Power Load Back Rate | installer
| 09CD | OvrtInVlot | U16 | 1 | % | 0 | 65535 | RW | EnterOVRTVoltage value percentage | installer
| 09CE | OvrtFirstPointVolt | U16 | 1 | % | 0 | 65535 | RW | High voltage ride through first point voltage percentage | installer
| 09CF | OvrtFirstPointTime | U16 | 10 | ms | 0 | 65535 | RW | High pressure crossing first time | installer
| 09D0 | OvrtSecondPointVolt | U16 | 1 | % | 0 | 65535 | RW | High Voltage Ride Through Second Point Voltage Percentage | installer
| 09D1 | OvrtSecondPointTime | U16 | 10 | ms | 0 | 65535 | RW | High pressure crossing second point time | installer
| 09D2 | OvrtThirdPointVolt | U16 | 1 | % | 0 | 65535 | RW | High voltage ride through the third point voltage percentage | installer
| 09D3 | OvrtThirdPointTime | U16 | 10 | ms | 0 | 65535 | RW | The third time of high pressure crossing | installer
| 09D4 | OvrtFourthPointVolt | U16 | 1 | % | 0 | 65535 | RW | High voltage ride through the fourth point voltage percentage | installer
| 09D5 | OvrtFourthPointTime | U16 | 10 | ms | 0 | 65535 | RW | The fourth time of high pressure crossing | installer
| 09D6 | OvrtReactiveCurrentCoefficientK | U16 | 0.1 | pu | 0 | 65535 | RW | High voltage ride through reactive current coefficientK | installer
| 09D7 | OvrtWaitingTimeAfterVoltageRecovery | U16 | 1 | ms | 0 | 65535 | RW | Waiting time after high pressure ride through recovery | installer
| 09D8 | OvrtPowerBackRate | U16 | 1 | %Pn/min | 1 | 300 | RW | High-voltage ride-through power backload rate | installer
| 09D9 | ZeroCurrentModeInLowVolt | U16 | 1 | % | 0 | 65535 | RW | Zero current mode enters low voltage percentage | installer
| 09DA | ZeroCurrentModeInHighVolt | U16 | 1 | % | 0 | 65535 | RW | Zero Current Mode Enters High Voltage Percentage | installer
| 09DB | LvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | Low Voltage Ride Through Exit Voltage Percentage | installer
| 09DC | LvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | Percentage of starting voltage value for low-voltage ride-through reactive current calculation | installer
| 09DD | OvrtOutVolt | U16 | 1 | % | 0 | 65535 | RW | Percentage of high voltage ride-through exit voltage value | installer
| 09DE | OvrtIqVoltStart | U16 | 1 | % | 0 | 65535 | RW | Percentage of initial voltage value for calculation of high-voltage ride-through reactive current | installer
| 09DF | MaxIqPct | U16 | 1 | % | 0 | 65535 | RW | Maximum reactive current percentage | installer
Island, GFCI, ISO parameters (0x0A00-0x0A3F)
| 0A00 | IslandConfig | U16 |  |  |  |  | RW | Bit0: Island Enable Register Bit1: Single-phase islanding enable (for three-phase inverters) | installer
| 0A01 | GFCIConfig | U16 |  |  |  |  | RW | Bit0:GFCIenable register | installer
| 0A02 | ISOConfig | U16 |  |  |  |  | RW | Bit0 : Insulation resistance enable registerBit1: Ground Detect Enable Register | installer
| 0A03 | InsulationProtectionValue | U16 | 1 | kΩ | 30 | 65535 | RW | Insulation resistance protection value | installer
| 0A04 | IsoLeakageCurrentLimit | U16 | 1 | mA | 1 | 50 | RW | Component Earth Leakage Current Limit | installer
| 0A05 | GFCILimit | U16 | 1 | mA/kVA | 1 | 50 | RW | Leakage current limit (not open for now, the setting is invalid) | installer
| 0A06 | PE_N_Config | U16 |  |  |  |  | RW | PEandNcontrol register Bit0:Off-gridPENShort enable bit Bit1:NLine detect enable bit | installer
| 0A07 | IslandDetectSensitivity | U16 |  |  |  |  | RW | Island Detection Sensitivity | installer
| 0A08 | PEProtectionValue | U16 | 1 | kΩ | 1000 | 65535 | RW | Ground fault judgment threshold | installer
0A09
0A0A
0A0B
0A0C
0A0D
Arc (0x0A40-0x0A7F)
| 0A40 | [8 empty] | installer
Parameter setting area (0x1000-0x17FF)
Basic parameter configuration (0x1000-0x10FF)
| 1000 | AddressMask_Config_Basic1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 1001 | [8 empty] | end user
| 1002 | [8 empty] | end user
| 1003 | [8 empty] | end user
| 1004 | SysTimeConfig_Year | U16 |  | year | 0 | 99 | RW | system time-year; the actual year is equal to2000+register value | end user
| 1005 | SysTimeConfig_Month | U16 |  | moon | 1 | 12 | RW | system time-month | end user
| 1006 | SysTimeConfig_Date | U16 |  | day | 1 | 31 | RW | system time-day | end user
| 1007 | SysTimeConfig_Hour | U16 |  | Time | 0 | 23 | RW | system time-Hour | end user
| 1008 | SysTimeConfig_Minute | U16 |  | Minute | 0 | 59 | RW | system time-minute | end user
| 1009 | SysTimeConfig_Second | U16 |  | second | 0 | 59 | RW | system time-second | end user
| 100A | SysTimeConfig_Control | U16 |  |  | 1 | 1 | RW | write value1 When , the value in the shadow register of the system time is updated to the actual system time; when reading, the state of the last write operation is returned:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter access failed0xFFFF: Operation failed, input parameters are incorrect | end user
| 100B | RS485Config_Address | U16 |  |  | 1 | 247 | RW | RS485configure-address | end user
| 100C | RS485Config_Baud | U16 |  |  | 0 | 4 | RW | RS485baud rate selection; 0:4800bps 1:9600bps(default) 2:19200bps 3:38400bps 4:57600bps 5:115200bps 10:1200bps 11:2400bps | end user
| 100D | RS485Config_StopBit | U16 |  |  | 0 | 2 | RW | RS485stop bit selection; 0:1 bit stop bit (default)1:1.5 bit stop bit2:2bit stop bit | end user
| 100E | RS485Config_ParityBit | U16 |  |  | 0 | 4 | RW | RS485Check digit selection; 0: no verification/None (default)1: Even parity/Even2:Odd parity/Odd3:high/Mark4:Low/Space | end user
| 100F | RS485Config_Control | U16 |  |  | 1 | 1 | RW | write value1hour,RS485The value in the configuration shadow register is updated to the systemRS485 In configuration; when reading, returns the status of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter access failed0xFFFF: Operation failed, input parameters are incorrect | end user
| 1010 | PV_InputMode_Config | U16 |  |  | 0 | 1 | RW | PVinput mode selection; 0 : Parallel mode1: Standalone mode (default) | installer
| 1011 | InputType_Channel0_Config | U16 |  |  | 0 | 255 | RW | input channel0type selection; value0Indicates that the current channel is not used; value1~127Indicates that the current channel is the input of photovoltaic panels; value128~255Indicates that the current channel is the battery input; if the value of two or more channels is the same and greater than zero, it indicates that these channels are input in parallel; | installer
| 1012 | InputType_Channel1_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1013 | InputType_Channel2_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1014 | InputType_Channel3_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1015 | InputType_Channel4_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1016 | InputType_Channel5_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1017 | InputType_Channel6_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1018 | InputType_Channel7_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1019 | InputType_Channel8_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 101A | InputType_Channel9_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 101B | InputType_Channel10_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 101C | InputType_Channel11_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 101D | InputType_Channel12_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 101E | InputType_Channel13_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 101F | InputType_Channel14_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1020 | InputType_Channel15_Config | U16 |  |  | 0 | 255 | RW |  | installer
| 1021 | InputType_Control | U16 |  |  | 1 | 1 | RW | write value1 When reading, the value in the shadow register of the input channel type is updated to the system input channel type configuration; when reading, the state of the last write operation is returned:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter access failed0xFFFF: Operation failed, input parameters are incorrect | installer
| 1022 | SafetyUpdateFromUSB_Control | U16 |  |  | 1 | 1 | RW | write value1, for the communication board fromUTake out the safety parameters from the disk; when reading, return the status of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter access failed0xFFFF: Operation failed, input parameters are incorrect | installer
| 1023 | AntiReflux_Control | U16 |  |  | 0 | 2 | RW | Anti-reverse flow enable control 0: Disable anti-reverse flow function 1: Default anti-reverse flow mode 2: Three-phase average power anti-reverse flow mode 3: Phase power mode | installer
| 1024 | AntiReflux_Power | U16 | 100 | W | 0 | 65535 | RW | Anti-backflow power | installer
| 1025 | IVCurveScan_Control | U16 |  |  | 0 | 1 | RW | IV curve scan enable control | installer
| 1026 | IVCurveScan_Period | U16 | 1 | minute | 5 | 65535 | RW | IVCurve scan period | installer
| 1027 | IVCurveScan_Oneshot | U16 |  |  | 1 | 1 | RW | IVCurve sweep is active; the written value is1, activate1Second-rateIVCurve scan; when reading, returns the state of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter access failed0xFFFF: Operation failed, input parameters are incorrect | installer
| 1028 | IVCurveScan_ReadChannel | U16 |  |  | 0 | 31 | RW | IVThe curve scan returns the data channel. This register is used to specifyIVCorresponding to the return value of the curve scan resultPVaisle. | installer
| 1029 | EPS_Control | U16 |  |  | 0 | 2 | RW | Emergency power supply enable control 0: Turn off emergency power supply (default) 1: Turn on emergency power supply, prohibit cold start 2: Turn on emergency power supply, enable cold start | end user
| 102A | EPS_WaitTime | U16 | 1 | second | 0 | 65535 | RW | Emergency power supply start waiting time (reservation function) | end user
| 102B | BatteryActive_Control | U16 |  |  | 0 | 1 | RW | Battery Auto Activation Enable Control | end user
| 102C | BatteryActive_Oneshot | U16 |  |  | 1 | 1 | RW | battery active; written value is1when, carry out1secondary battery activation; When reading, returns the status of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter storage failed0xFFFF: Operation failed, input parameters are incorrect | end user
| 102D | CT_Auto_Calibrate | U16 |  |  | 1 | 1 | RW | CTAutomatic correction; the written value is1when, carry out1Second-rateCT Automatic correction; when reading, returns the state of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD Operation failed, the current function is disabled0xFFFE : Operation failed, parameter storage failed0xFFFF: Operation failed, input parameters are incorrect | installer
| 102E | Italy_AutoTest | U16 |  |  | 1 | 2 | RW | Italian automatic test writes:0x0001: perform standard tests(S) ;0x0002: perform a quick test(F) ; When reading, returns the status of the last write operation:0x0000 :success0x0001 : Standard test in operation0x0002 : Running quick test0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter storage failed0xFFFF: Operation failed, input parameters are incorrect | installer
| 102F |  | U16 |  |  |  |  | RW |  | installer
| 1030 | EnergyStatistics_Date_Year | U16 | 1 | year | 0 | 19 | RW | Electric energy statistics return date setting register. This register specifies the year of the returned energy data. Year refers to the latest Nth year relative to the inverter system time. N is the register value. 0: the current year of the system time; 1: 1 year before the system time; … 19: 19 years before the system time. | installer
| 1031 | EnergyStatistics_Date_Month | U16 | 1 | moon | 1 | 12 | RW | Electric energy statistics return date setting register. This register specifies the month of the returned energy data. | installer
| 1032 | EnergyStatistics_Date_Date | U16 | 1 | day | 1 | 31 | RW | Electric energy statistics return date setting register. This register specifies the day and minute of the returned energy data. | installer
| 1033 | EnergyStatistics_Config | U16 |  |  |  |  | RW | Electric energy statistics return setting register. High byte: The date and time setting of the returned data. 0x01: Daily, the first 24 pieces of data in the return area are valid; 0x02: Monthly, the first 31 pieces of data in the return area are valid; 0x03: Every year, the first 12 pieces of data in the return area are valid; 0x04: Life cycle, before the return area 20 pieces of data are valid; others: invalid. Low byte: The physical quantity setting of the returned data. 0x01: PV power generation; 0x02: Load power consumption; 0x03: System buy power; 0x04: System sell power; 0x05: Battery charge; 0x06: Battery discharge; Others: Invalid. | installer
| 1034 | Language | U16 |  |  | 0 | 65535 | RW | Inverter menu language number setting register. 0: Chinese 1: English 2: Italian 3: German 4: French 5: Portuguese 6: Ukrainian 7: Slovak 8: Spanish 9: Finnish 10: Polish 11: Korean 12: Japanese 13: Russian arts | end user
| 1035 | Parallel_Control | U16 |  |  | 0 | 2 | RW | 0: Disable parallel function 1: Enable AC parallel function 2: Enable AC+BAT parallel function | installer
| 1036 | Parallel_Master_Slave | U16 |  |  | 0 | 1 | RW | 0: The machine is configured as a slave 1: The machine is configured as a master (default) | installer
| 1037 | Parallel_Address | U16 |  |  | 0 | 10 | RW | Local parallel address | installer
| 1038 | UnbalancedSupport_Control | U16 |  |  | 0 | 1 | RW | 3-phase 4-wire mode grid unbalanced support control register 0: Disable unbalanced support function (default) 1: Enable unbalanced support function | installer
| 1039 | PV_Generation_Ratio | U16 | 0.001 | pu | 800 | 3600 | RW | Power generation multiplier. Default value 1000 | installer
| 103A | Energy_Purchase_Ratio | U16 | 0.001 | pu | 800 | 1500 | RW | Buy power multiplier. Default value 1000 | installer
| 103B | Energy_Selling_Ratio | U16 | 0.001 | pu | 800 | 1500 | RW | Selling power rate. Default value 1000 | installer
| 103C | Bat_Charge_Ratio | U16 | 0.001 | pu | 800 | 1500 | RW | Charge rate. Default value 1000 | installer
| 103D | Bat_Discharge_Ratio | U16 | 0.001 | pu | 800 | 1500 | RW | Discharge rate. Default value 1000 | installer
| 103E | LogicInterface_Control | U16 |  |  | 0 | 1 | RW | Logic Interface Control Register 0: disable 1:Enable | installer
103F
| 1040 | AddressMask_Config_Basic2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 1041 | [8 empty] | end user
| 1042 | [8 empty] | end user
| 1043 | [8 empty] | end user
| 1044 | BatConfig_ID | U16 |  |  | 0 | 7 | RW | battery serial number. The serial number specified by this register corresponds to the actual battery input interface of the inverter. After successfully writing this register, the battery parameters will be updated to the parameters corresponding to the written serial number. | end user
| 1045 | BatConfig_Address | U16 |  |  | 0 | 99 | RW | battery address. If multiple groups of batteries are allowed to be connected in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | end user
| 1046 | BatConfig_Potocol | U16 |  |  | 0 | 65535 | RW | Battery parameters-communication protocol 0: First flight built-in BMS/DEFAULT 1: Pylon protocol/PYLON 2: First flight protocol/GENERAL 3: AMASS 4: LG 5: Alpha.ESS 6: CATL 7: Weco 8: Fronus 9: EMS 10: Nilar11: BTS 5K 12: Action | end user
| 1047 | BatConfig_Voltage_Over | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters - overvoltage protection value | installer
| 1048 | BatConfig_Voltage_Charge | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters - charging voltage | installer
| 1049 | BatConfig_Voltage_Lack | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters - under-voltage protection voltage lead-acid battery is visible | installer
| 104A | BatConfig_Voltage_Discharge_Stop | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters-Minimum discharge voltage | installer
| 104B | BatConfig_Current_Charge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery parameters-Maximum Charge Current Limit | end user
| 104C | BatConfig_Current_Discharge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery parameters-Maximum discharge current limit | end user
| 104D | BatConfig_Depth_of_Discharge | U16 | 1 | % | 1 | 90 | RW | DODIndicates the maximum discharge amount when the grid is normal, whenSOC<1-DOD When the inverter stops discharging, the inverter will also stop discharging according to other conditions;DOD<=EOD | end user
| 104E | BatConfig_End_of_Discharge | U16 | 1 | % | 1 | 90 | RW | EODIndicates the off-grid maximum discharge, whenSOC<1-EODWhen the inverter stops discharging, the inverter will also stop discharging according to other conditions. | end user
| 104F | BatConfig_Capacity | U16 | 1 | Ah | 1 | 65535 | RW | Battery parameters-Battery capacity (default 50) | end user
| 1050 | BatConfig_Voltage_Nominal | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters - rated battery voltage (default 0) | end user
| 1051 | BatConfig_Cell_Type | U16 | 1 |  | 0 | 6 | RW | Battery parameters-cell type; 0: lead acid (custom) 1: lithium iron phosphate 2: ternary 3: lithium titanate 4: AGM 5: Gel 6: Flooded | end user
| 1052 | BatConfig_EPS_Buffer | U16 | 1 | % | 5 | 100 | RW | Battery parameters - off-grid recovery discharge hysteresis; EPS_Buffer is not greater than EOD | end user
| 1053 | BatConfig_Control | U16 |  |  |  |  | RW | Battery parameter write control; the write value is1 When , the value in the battery parameter shadow register is updated to the system battery parameter configuration;write value2, the value in the battery parameter shadow register is updated toBatConfig_Potocolthe default value of ; When reading, returns the status of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter storage failed0xFFFF: Operation failed, input parameters are incorrect | end user
| 1054 | BatConfig_Address2 | U16 |  |  | 0 | 99 | RW | Battery address 2. If multiple groups of batteries are allowed to be connected in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | end user
| 1055 | BatConfig_Address3 | U16 |  |  | 0 | 99 | RW | Battery address 3. If multiple groups of batteries are allowed to be connected in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | end user
| 1056 | BatConfig_Address4 | U16 |  |  | 0 | 99 | RW | Battery address 4. If multiple groups of batteries are allowed to be connected in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | end user
| 1057 | BatConfig_TEMPCO | I16 | 0.1 | mV/Cell | -60 | 0 | RW | Battery parameters - lead-acid battery temperature compensation coefficient. | end user
| 1058 | BatConfig_Voltage_Recovery_Buffer | U16 | 0.1 | V |  |  | RW | Battery Parameters - Lead-acid battery recovery discharge voltage increment. Such as: stop discharging when "battery voltage < minimum discharge voltage"; resume discharging when "battery voltage> minimum discharge voltage + recovery discharge voltage increment". | end user
| 1059 | BatConfig_Control_Bits | U16 |  |  |  |  | RW | Battery parameter-function control bit Bit0: SOC control disabled (0: use SOC; 1: disable SOC) | end user
| 105A | BatConfig_Voltage_Float | U16 | 0.1 | V |  |  | RW | Battery parameters - lead-acid battery float voltage
105B
105C
105D
105E
105F
| 1060 | PCCSampleMode | U16 |  |  | 0 | 2 | RW | PCCPower Harvesting Device Configuration 0:Do not use 1: Electricity meter 2:CT 3:ARPC | end user
| 1061 | Resonance_Sensitivity | U16 |  |  | 1 | 100 | RW | Resonance detection sensitivity | end user
| 1062 | CT_rate | U16 |  |  |  |  | RW | CTRatio setting
| 1063 | Hard_Reflux_Config | U16 |  |  |  |  | RW | Hard anti-backflow switch: 0 disables/1use
1064
1065
1066
1067
1068
1069
106A
106B
106C
106D
106E
106F
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
107A
107B
107C
107D
107E
107F
| 1080 | AddressMask_Config_Basic3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 1081 | [8 empty] | installer
| 1082 | [8 empty] | installer
| 1083 | [8 empty] | installer
| 1084 | ArcingAlarmEnable | U16 |  |  | 1 |  | RW | Enable arc detection function | installer
| 1085 | PeakToPeakSet | U16 | 1 |  | 0x64 |  | RW | Peak-to-peak setting | installer
| 1086 | VarianceSet | U16 | 1 |  | 0x95 |  | RW | Variance setting | installer
| 1087 | HarmonicEnergySet | U16 | 1 |  | 0x01 |  | RW | Harmonic energy setting | installer
| 1088 | AmplitudeVarianceSet | U16 | 1 |  | 0x01 |  | RW | Amplitude variance setting | installer
| 1089 | TimeDomWeiSet | U16 | 1 |  | 0x01 |  | RW | Time domain weight setting | installer
| 108A | FreDomWeiSet | U16 | 1 |  | 0x05 |  | RW | Frequency domain weight setting | installer
| 108B | ArcDetectSensitivity | U16 | 1 |  | 0x14 |  | RW | Arc Detection Sensitivity | installer
| 108C | ArcAlarmShutdownThreshold | U16 | 1 |  | 0x05 |  | RW | Arc Alarm Count Shutdown Threshold | installer
| 108D | ArcSelfCheckCommand | U16 |  |  | 0x01 |  | RW | Write 1Indicates to start self-test (self-test all channels). It is automatically cleared after the self-test is over. | installer
| 108E | ArcingAlarmClear | U16 | 1 |  | 0x1234 | 0x1234 | RW | write 0x1234Clear arc alarm(all channels) | installer
| 108F | ArcAlarmCnt | U16 | 1 |  |  |  | RW | Arc Alarm Count
| 1090 | AfciResult | U16 | 1 |  |  |  | R | handshake result
| 1091 | SelfCheckResult | U16 |  |  |  |  | R | Bit0—aisle1Self-test results (0Self-check is successful;1 Self-test failed or no self-test)Bit1—aisle2, Bit2—aisle3, Bit3—aisle4, Bit4—aisle5, Bit5—aisle6,
| 1092 | SelfCheckState | U16 |  |  |  |  | R | Channel self-test status0 : no self-test1 : Self-checking2 : Self-check completed
1093
1094
1095
1096
1097
1098
1099
109A
109B
109C
109D
109E
109F
| 10A0 | PLC_Enable_Setting | U16 |  |  |  |  | RW
| 10A1 | PLC_Com_Property | U16 | NULL | NULL | 0 |  | RW | bit0-bot1: 0~1correspond 1/1.5 bit2~bit4:0~7correspondNONE/odd/EVENThree verification methods bit5~bit7 0~3correspond8/9lTwo data bit lengths bit8~15 0~7correspond 4800/9600/19200/38400/115200 | end user
10A2
10A3
10A4
| 10A5 | BLE_Enable_Setting | U16 | NULL | NULL | 0 | 1 | RW
| 10A6 | BLE_Com_Property | U16 | NULL | NULL | 0 | 65535 | RW | bit0-bot1: 0~1correspond 1/1.5 bit2~bit4:0~7correspondNONE/odd/EVENThree verification methods bit5~bit7 0~1correspond8/9lTwo data bit lengthsbit8~15 0~7correspond 4800/9600/19200/38400/115200
10A7
10A8
10A9
10AA
10AB
10AC
10AD
10AE
10AF
| 10B0 | PID_Auto_running_enable | U16 |  |  | 0 | 1 | RW | PIDStart autorun. 0means disabled;1Indicates enable. | end user
| 10B1 | PID_Working_Start_Time | BCD16 | 1 | Minute | 0 | 2359 | RW | PIDwork start time(BCDcode).For example: minimum value0x0000express00:00;maximum value0x2359express23:59. | end user
| 10B2 | PID_Working_Hours | U16 | 1 | Minute | 0 | 65535 | RW | PIDwork time. | end user
| 10B3 | PID_Working_PV_Threshold | U16 | 0.1 | V | 0 | 65535 | RW | PIDstart upPVvalue threshold.whenPVOnly allowed when the voltage is below the thresholdPIDstart up. | end user
| 10B4 | PID_Break_Restart_Delay | U16 | 1 | Minute | 0 | 65535 | RW | PIDRestart wait time after fault shutdown. | end user
10B5
10B6
10B7
10B8
10B9
10BA
10BB
10BC
10BD
10BE
10BF
10C0
10C1
10C2
10C3
10C4
10C5
10C6
10C7
10C8
10C9
10CA
10CB
10CC
10CD
10CE
10CF
10D0
10D1
10D2
10D3
10D4
10D5
10D6
10D7
10D8
10D9
10DA
10DB
10DC
10DD
10DE
10DF
10E0
10E1
10E2
10E3
10E4
10E5
10E6
10E7
10E8
10E9
10EA
10EB
10EC
10ED
10EE
10EF
10F0
10F1
10F2
10F3
10F4
10F5
10F6
10F7
10F8
10F9
10FA
10FB
10FC
10FD
10FE
10FF
Remote control (0x1100-0x12FF)
| 1100 | AddressMask_Config_Remote1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 1101 | [8 empty] | end user
| 1102 | [8 empty] | end user
| 1103 | [8 empty] | end user
| 1104 | Remote_On_Off_Control | U16 |  |  | 0 | 1 | RW | Remote switch. 0x0000: Power off 0x0001: Power on | end user
| 1105 | Power_Control | U16 |  |  |  |  | RWV | Power control; Bit0: Active enable bit Bit1: Reactive enable bit Bit2: Reactive mode selection bit (0: Reactive_Power; 1: Power_Factor) Bit3: SVG enable bit Bit4: SVG reactive mode selection bit (0: Fixed_Reactive_Power ; 1: Reactive_Power) | end user | ① Enables broadcast control of active and reactive power 00 10 11 05 00 01 02 00 03 EA 95 ② Set active power 22KW 00 10 11 06 00 01 02 00 C8 AB 31
| 1106 | Active_Power_Export_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | Output maximum active power percentage | end user | 4358
| 1107 | Active_Power_Import_Limit | U16 | 0.1 | % | 0 | 1000 | RWV | Enter the maximum active power percentage | end user
| 1108 | Reactive_Power_Setting | I16 | 0.1 | % | -1000 | 1000 | RWV | Reactive power percentage. Note: The maximum reactive power is limited by the specific model. | end user
| 1109 | Power_Factor_Setting | I16 | 0.01 | pu | -100 | 100 | RWV | power factor. Note: The minimum power factor is limited by the specific model. | end user
| 110A | Active_Power_Limit_Speed | U16 | 1 | % | 1 | 65535 | RWV | Active power limit change rate | end user
| 110B | Reactive_Power_Response_Time | U16 | 0.1 | second | 0 | 65535 | RWV | Reactive power setting response time | end user
| 110C | SVG_Fixed_Reactive_Power_Setting | I16 | 0.1 | kVar | -32768 | 32767 | RWV | SVGFixed reactive power size in mode | end user
| 110D | [8 empty] | end user
| 110E | [8 empty] | end user
| 110F | [8 empty] | end user
| 1110 | Energy_Storage_Mode_Control | U16 |  |  | 0 | 4 | RW | Energy storage working mode setting; 0 : Spontaneous self-use mode1 : Time-of-use tariff model2 : Timed charging and discharging mode3 : passive mode4: Peak clipping mode 5: Off-grid mode 6: Generator mode is used to change the working mode. | end user
| 1111 | Timing_ID | U16 |  |  | 0 | 3 | RW | Timing charge and discharge - rule sequence number; the smaller the sequence number, the higher the priority. After successfully writing to this register, the timing charging and discharging parameters will be updated to the parameters corresponding to the written serial number. | end user
| 1112 | Timing_On_Off_Control | U16 |  |  | 0 | 1 | RW | Timing charge and discharge - enable control; Bit0: charge enable Bit1: discharge enable | end user
| 1113 | Timing_Charge_Start | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | high byte. Low byte of charging start hour. Charge start minutes | end user
| 1114 | Timing_Charge_End | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | high byte. End of charge hour low byte. Charge end minutes | end user
| 1115 | Timing_Discharge_Start | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | high byte. Discharge start hour low byte. Discharge start minutes | end user
| 1116 | Timing_Discharge_End | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | high byte. Discharge end hour low byte. Discharge end minutes | end user
| 1117 | Timing_Power_Charge | U32 | 1 | W | 1 | 4294967296 | RW | Timed charge and discharge-charging power | end user
| 1118 | [8 empty] | end user
| 1119 | Timing_Power_Discharge | U32 | 1 | W | 1 | 4294967296 | RW | Timed charge and discharge-Discharge power | end user
| 111A | [8 empty] | end user
| 111B | Timing_Rsvd1 | [6 empty] | Timed charging and discharging - reserved 1 | end user
| 111C | Timing_Rsvd2 | [6 empty] | Timed charging and discharging - reserved 2 | end user
| 111D | Timing_Rsvd3 | [6 empty] | Timed charging and discharging - reserved 3 | end user
| 111E | Timing_Rsvd4 | [6 empty] | Timed charging and discharging - reserved 4 | end user
| 111F | Timing_Control | U16 |  |  | 1 | 1 | RW | Timing charge and discharge write control; the write value is1 When , the value in the shadow register of timing charge and discharge is updated to the system timing charge and discharge configuration; when read, it returns the state of the last write operation:0x0000 :success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE Operation failed, parameter storage failed0xFFFF: Operation failed, input parameters are incorrect | end user
| 1120 | TOU_ID | U16 |  |  | 0 | 7 | RW | Time-of-use electricity price-rule serial number; the smaller the serial number, the higher the priority. After the register is successfully written, the time-of-use electricity price parameter will be updated to the parameter corresponding to the written serial number. | end user
| 1121 | TOU_On_Off_Control | U16 |  |  | 0 | 1 | RW | Time-of-use electricity price - rule enable; 0: disable 1: enable | end user
| 1122 | TOU_Charge_Start | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | high byte. Low byte of charging start hour. Charge start minutes | end user
| 1123 | TOU_Charge_End | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | high byte. End of charge hour low byte. Charge end minutes | end user
| 1124 | TOU_Charge_Target_SOC | U16 | 1 | % | 30 | 100 | RW | time-of-use tariff-Forced charge cut-offSOC; Remaining power percentage, when the battery is currentlySOCWhen this register value is reached, the forced charging ends and the self-use mode is entered, and the discharge is prohibited at the same time. | end user
| 1125 | TOU_Charge_Power | U32 | 1 | W | 1 | 4294967296 | RW | Time-of-use electricity price - mandatory charging power; the setting value cannot exceed the rated power of the machine. | end user
| 1126 | [8 empty] | end user
| 1127 | TOU_Executed_Date_Start | U16 | 1 1 | Month Day | 1 1 | 12 31 | RW | high byte. The low byte of the month the rule takes effect. Rule effective date | end user
| 1128 | TOU_Executed_Date_End | U16 | 1 1 | Month Day | 1 1 | 12 31 | RW | high byte. The low byte of the month the rule stops taking effect. Rule ceases to take effect | end user
| 1129 | TOU_Executed_Day_of_Week | U16 |  |  |  |  | RW | time-of-use tariff-The week the rule takes effect; the register is represented by a bit field, and the bits are0Indicates the invalid week, the bit is1 Indicates the effective weekBit0 :MondayBit1 :TuesdayBit2 :WednesdayBit3 :ThursdayBit4 :FridayBit5 :SaturdayBit6:Sunday | end user
| 112A | TOU_Rsvd1 | [6 empty] | Time-of-use tariff - reserved 1 | end user
| 112B | TOU_Rsvd2 | [6 empty] | Time-of-use tariff - reserved 2 | end user
| 112C | TOU_Rsvd3 | [6 empty] | Time-of-use tariff - reserve 3 | end user
| 112D | TOU_Rsvd4 | [6 empty] | Time-of-use tariff - reserve 4 | end user
| 112E | TOU_Rsvd5 | [6 empty] | Time-of-use tariff - reserve 5 | end user
| 112F | TOU_Control | U16 |  |  | 1 | 1 | RW | time-of-use tariff-write control; the write value is1 When the value in the shadow register of the time-of-use electricity price is updated to the system time-of-use electricity price configuration; when reading, the state of the last write operation is returned:0x0000:success0x0001 : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter storage failed0xFFFF: Operation failed, input parameters are incorrect | end user
| 1130 | Peak_Shaving_Discharge_Threshold | U32 | 1 | W | 100 |  | RW | The power cap that allows the system to buy electricity from the grid | end user
| 1131 | [8 empty] | end user
| 1132 | Peak_Shaving_Charge_Threshold | U32 | 1 | W | 100 |  | RW | The power cap that allows the system to sell electricity to the grid | end user
| 1133 | [8 empty] | end user
1134
1135
1136
1137
1138
1139
113A
113B
113C
113D
113E
113F
| 1140 | AddressMask_Config_Remote2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 1141 | [8 empty] | end user
| 1142 | [8 empty] | end user
| 1143 | [8 empty] | end user
| 1144 | Off_Grid_Charge_Source | U16 |  |  | 0 | 2 | RW | Off-grid mode -Charging source selection: 0: Grid 1: Generator 2: Reserved
| 1145 | Off_Grid_Grid_Power | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode -Power taken from grid
| 1146 | Off_Grid_DG_Power | U16 | 0.01 | kW | 0 | 65535 | RW | Off-grid mode -Generator maximum power
| 1147 | Dry_Contact | U16 |  |  | 0 | 3 | RW | Dry contact control 0: disable dry contact; 1: generator mode; 2: Relay mode1(off-grid output is high, the rest are low); 3: Relay mode2(off-grid output is low, the rest are high);
1148
1149
114A
114B
114C
114D
114E
114F
1150
1151
1152
1153
1154
1155
1156
1157
1158
1159
115A
115B
115C
115D
115E
115F
1160
1161
1162
1163
1164
1165
1166
1167
1168
1169
116A
116B
116C
116D
116E
116F
1170
1171
1172
1173
1174
1175
1176
1177
1178
1179
117A
117B
117C
117D
117E
117F
| 1180 | AddressMask_Config_Remote3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 1181 | [8 empty] | end user
| 1182 | [8 empty] | end user
| 1183 | [8 empty] | end user
| 1184 | Passive_Timeout | U16 | 1 | second | 0 | 65535 | RW | passive mode-timeout control; default:0; Set the communication timeout time in passive mode. When the inverter does not receive any communication within the time set by this register, the inverter will enforce the timeout action. special, write to this register0The timeout feature will be disabled. | end user
| 1185 | Passive_Timeout_Action | U16 |  |  | 0 | 1 | RW | passive mode-timeout action; 0 : Forced standby1: Force recovery to the energy storage mode before entering passive mode | end user
| 1186 | Passive_Rsvd1 | [6 empty] | passive mode-reserved1 | end user
| 1187 | Passive_Manual_Gdes | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode desired grid power (Gdes); positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 1188 | [8 empty] | end user
| 1189 | Passive_Manual_Blo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode battery minimum charge and discharge power (Blo); positive value means charging; negative value means discharging. | end user
| 118A | [8 empty] | end user
| 118B | Passive_Manual_Bup | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charging and discharging power (Bup) of the battery in Manual mode; a positive value means charging; a negative value means discharging. | end user
| 118C | [8 empty] | end user
| 118D | Passive_Manual_Gdzup | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows selling electrical power (Gdzup); positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 118E | [8 empty] | end user
| 118F | Passive_Manual_Gdzlo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows buying electrical power (Gdzlo); positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 1190 | [8 empty] | end user
| 1191 | Passive_Scheduler_Gdes_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Ante); Scheduled task parameter, valid within the scheduled time period. Positive values indicate power direction"From grid to system"Negative values indicate power direction"From system to grid". | end user
| 1192 | [8 empty] | end user
| 1193 | Passive_Scheduler_Blo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode battery minimum charge and discharge power (Blo_Ante); Scheduled task parameters, valid within the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 1194 | [8 empty] | end user
| 1195 | Passive_Scheduler_Bup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode battery maximum charge and discharge power (Bup_Ante); Scheduled task parameters, valid within the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 1196 | [8 empty] | end user
| 1197 | Passive_Scheduler_Gdzup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows selling power (Gdzup_Ante); Scheduled task parameters, valid within the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 1198 | [8 empty] | end user
| 1199 | Passive_Scheduler_Gdzlo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Ante); Scheduled task parameters, valid within the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 119A | [8 empty] | end user
| 119B | Passive_Scheduler_Gdes_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Post); Scheduled task parameters, valid after the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 119C | [8 empty] | end user
| 119D | Passive_Scheduler_Blo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode battery minimum charge and discharge power (Blo_Post); Scheduled task parameters, valid after the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 119E | [8 empty] | end user
| 119F | Passive_Scheduler_Bup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode battery maximum charge and discharge power (Bup_Post); Scheduled task parameters, valid after the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 11A0 | [8 empty] | end user
| 11A1 | Passive_Scheduler_Gdzup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows selling power (Gdzup_Post); Scheduled task parameters, valid after the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 11A2 | [8 empty] | end user
| 11A3 | Passive_Scheduler_Gdzlo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Post); Scheduled task parameters, valid after the scheduled time period. Positive values indicate power direction"From grid to system"; Negative values indicate power direction"From system to grid". | end user
| 11A4 | [8 empty] | end user
| 11A5 | Passive_Scheduler_StartTime | U32 | 1 | second | 0 | 4294967296 | RW | Scheduler mode applies the start time of the expected parameter setting value; StartTime is in unix time format, because the internal time of the system is Greenwich Mean Time (GMT) by default, so when setting this parameter, you should pay attention to the local time zone of the country where you are located, StartTime=(local time) Unix Time) ± (seconds corresponding to the time difference between local time and UTC/GMT) | end user
| 11A6 | [8 empty] | end user
| 11A7 | Passive_Scheduler_DurationTime | U32 | 1 | second | 0 | 4294967296 | RW | SchedulerThe duration for which the mode applies the desired parameter set value(DurationTime) | end user
| 11A8 | [8 empty] | end user
| 11A9 | Passive_Scheduler_ManagementMode | U16 |  |  | 0 | 2 | RW | SchedulerMode management mode selection(ManagementMode); 0 : Spontaneous self-use mode1:Manual model2:SchedulerMode can only be entered0,1,2, other data is invalid. | end user
11AA
11AB
11AC
11AD
11AE
11AF
11B0
11B1
11B2
11B3
11B4
11B5
11B6
11B7
11B8
11B9
11BA
11BB
11BC
11BD
11BE
11BF
| 11C0 | AddressMask_Config_Remote4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | end user
| 11C1 | [8 empty] | end user
| 11C2 | [8 empty] | end user
| 11C3 | [8 empty] | end user
| 11C4 | CommBreak_Protect_Enable | U16 | 1 |  | 0 | 65535 | RW | Power station communication interruption protection function enable register:0: The power station communication interruption protection function is disabled (default)1: The power station communication interruption protection function is enabled
| 11C5 | CommBreak_Recovery_Mode | U16 | 1 |  | 0 | 65535 | RW | Power station communication interruption protection recovery method:0: automatic recovery (default)1: Manual recovery
| 11C6 | CommBreak_Threshold_Time | U16 | 1 | min | 10 | 120 | RW | Power station communication interruption threshold time:10-120min (default: 15min)
| 11C7 | CommBreak_Mode_Judge | U16 | 1 |  | 0 | 65535 | RW | Power station communication interruption data monitoring source:0:485 (default)1: WIFI3: PLC
| 11C8 | CommBreak_Alarm_Clear | U16 | 1 |  | 0 | 65535 | W | Power station communication interruption alarm clear register:Write a value of "1" to clear the communication interruption alarm status
The inverter returns read-only results (0x1300-0x15FF)
| 1300 | AddressMask_Config_ReadOnly_Result1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
1301
1302
1303
| 1304 | Italay_Autotest_Result1 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection value is set by default.
| 1305 | Italay_Autotest_Result2 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection time is set by default.
| 1306 | Italay_Autotest_Result3 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. The test result of the first-level overvoltage protection value.
| 1307 | Italay_Autotest_Result4 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. Level 1 overvoltage protection time test results.
| 1308 | Italay_Autotest_Result5 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. By default, the secondary overvoltage protection value is set.
| 1309 | Italay_Autotest_Result6 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. By default, the secondary overvoltage protection time is set.
| 130A | Italay_Autotest_Result7 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. The test result of the secondary overvoltage protection value.
| 130B | Italay_Autotest_Result8 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. Secondary overvoltage protection time test results.
| 130C | Italay_Autotest_Result9 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection value is set by default.
| 130D | Italay_Autotest_Result10 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection time is set by default.
| 130E | Italy_Autotest_Result11 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The test result of the first-level undervoltage protection value.
| 130F | Italay_Autotest_Result12 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s1. Level 1 undervoltage protection time test results.
| 1310 | Italay_Autotest_Result13 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. By default, the secondary undervoltage protection value is set.
| 1311 | Italay_Autotest_Result14 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. By default, the secondary undervoltage protection time is set.
| 1312 | Italay_Autotest_Result15 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s2. The test result of the secondary undervoltage protection value.
| 1313 | Italay_Autotest_Result16 | U16 | 1 | ms |  |  | R | Italian automatic test 27.s2. Secondary undervoltage protection time test results.
| 1314 | Italay_Autotest_Result17 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s1. The first-level overfrequency protection value is set by default.
| 1315 | Italay_Autotest_Result18 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s1. The first-level overfrequency protection time is set by default.
| 1316 | Italay_Autotest_Result19 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s1. The test result of the first-level overfrequency protection value.
| 1317 | Italay_Autotest_Result20 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s1. Level 1 overfrequency protection time test results.
| 1318 | Italay_Autotest_Result21 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s2. The second-level overfrequency protection value is set by default.
| 1319 | Italay_Autotest_Result22 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s2. The second-level overfrequency protection time is set by default.
| 131A | Italay_Autotest_Result23 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81>s2. The test result of the secondary overfrequency protection value.
| 131B | Italay_Autotest_Result24 | U16 | 1 | ms |  |  | R | Italian automatic test 81>s2. Test results of secondary overfrequency protection time.
| 131C | Italy_Autotest_Result25 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s1. The first-level underfrequency protection value is set by default.
| 131D | Italay_Autotest_Result26 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s1. The first-level underfrequency protection time is set by default.
| 131E | Italy_Autotest_Result27 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s1. The test result of the first-level underfrequency protection value.
| 131F | Italay_Autotest_Result28 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s1. The test results of the first-level underfrequency protection time.
| 1320 | Italay_Autotest_Result29 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s2. The second-level underfrequency protection value is set by default.
| 1321 | Italay_Autotest_Result30 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s2. The second-level underfrequency protection time is set by default.
| 1322 | Italay_Autotest_Result31 | U16 | 0.01 | Hz |  |  | R | Italian automatic test 81<s2. The test result of the secondary underfrequency protection value.
| 1323 | Italay_Autotest_Result32 | U16 | 1 | ms |  |  | R | Italian automatic test 81<s2. Test results of secondary underfrequency protection time.
| 1324 | Italay_Autotest_Result33 | [6 empty] | Italian automatic test results 33
| 1325 | Italay_Autotest_Result34 | [6 empty] | Italian automatic test results 34
| 1326 | Italay_Autotest_Result35 | [6 empty] | Italian automatic test results 35
| 1327 | Italay_Autotest_Result36 | [6 empty] | Italian automatic test results 36
| 1328 | Italay_Autotest_Result37 | [6 empty] | Italian automatic test results 37
| 1329 | Italay_Autotest_Result38 | [6 empty] | Italian automatic test results 38
| 132A | Italay_Autotest_Result39 | [6 empty] | Italian automatic test results 39
| 132B | Italay_Autotest_Result40 | [6 empty] | Italian automatic test results 40
| 132C | Italay_Autotest_Result41 | [6 empty] | Italian automatic test results 41
| 132D | Italay_Autotest_Result42 | [6 empty] | Italian automatic test results 42
| 132E | Italay_Autotest_Result43 | [6 empty] | Italian automatic test results 43
| 132F | Italay_Autotest_Result44 | [6 empty] | Italian automatic test results 44
| 1330 | Italay_Autotest_Result45 | [6 empty] | Italian automatic test results 45
| 1331 | Italay_Autotest_Result46 | [6 empty] | Italian automatic test results 46
| 1332 | Italay_Autotest_Result47 | [6 empty] | Italian automatic test results 47
| 1333 | Italay_Autotest_Result48 | [6 empty] | Italian automatic test results 48
| 1340 | AddressMask_Config_ReadOnly_Result2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
1341
1342
1343
| 1344 | IVCurve_Voltage1 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 1
| 1345 | IVCurve_Current1 | U16 | 0.01 | A |  |  | R | IV curve sweep current 1
| 1346 | IVCurve_Voltage2 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 2
| 1347 | IVCurve_Current2 | U16 | 0.01 | A |  |  | R | IV curve sweep current 2
| 1348 | IVCurve_Voltage3 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 3
| 1349 | IVCurve_Current3 | U16 | 0.01 | A |  |  | R | IV curve sweep current 3
| 134A | IVCurve_Voltage4 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 4
| 134B | IVCurve_Current4 | U16 | 0.01 | A |  |  | R | IV curve sweep current 4
| 134C | IVCurve_Voltage5 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 5
| 134D | IVCurve_Current5 | U16 | 0.01 | A |  |  | R | IV curve sweep current 5
| 134E | IVCurve_Voltage6 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 6
| 134F | IVCurve_Current6 | U16 | 0.01 | A |  |  | R | IV curve sweep current 6
| 1350 | IVCurve_Voltage7 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 7
| 1351 | IVCurve_Current7 | U16 | 0.01 | A |  |  | R | IV curve sweep current 7
| 1352 | IVCurve_Voltage8 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 8
| 1353 | IVCurve_Current8 | U16 | 0.01 | A |  |  | R | IV curve sweep current 8
| 1354 | IVCurve_Voltage9 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 9
| 1355 | IVCurve_Current9 | U16 | 0.01 | A |  |  | R | IV curve sweep current9
| 1356 | IVCurve_Voltage10 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 10
| 1357 | IVCurve_Current10 | U16 | 0.01 | A |  |  | R | IV curve sweep current 10
| 1358 | IVCurve_Voltage11 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 11
| 1359 | IVCurve_Current11 | U16 | 0.01 | A |  |  | R | IV curve sweep current 11
| 135A | IVCurve_Voltage12 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 12
| 135B | IVCurve_Current12 | U16 | 0.01 | A |  |  | R | IV curve sweep current 12
| 135C | IVCurve_Voltage13 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 13
| 135D | IVCurve_Current13 | U16 | 0.01 | A |  |  | R | IV curve sweep current 13
| 135E | IVCurve_Voltage14 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 14
| 135F | IVCurve_Current14 | U16 | 0.01 | A |  |  | R | IV curve sweep current 14
| 1360 | IVCurve_Voltage15 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 15
| 1361 | IVCurve_Current15 | U16 | 0.01 | A |  |  | R | IV curve sweep current 15
| 1362 | IVCurve_Voltage16 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 16
| 1363 | IVCurve_Current16 | U16 | 0.01 | A |  |  | R | IV curve sweep current 16
| 1364 | IVCurve_Voltage17 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 17
| 1365 | IVCurve_Current17 | U16 | 0.01 | A |  |  | R | IV curve sweep current 17
| 1366 | IVCurve_Voltage18 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 18
| 1367 | IVCurve_Current18 | U16 | 0.01 | A |  |  | R | IV curve sweep current 18
| 1368 | IVCurve_Voltage19 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 19
| 1369 | IVCurve_Current19 | U16 | 0.01 | A |  |  | R | IV curve sweep current 19
| 136A | IVCurve_Voltage20 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 20
| 136B | IVCurve_Current20 | U16 | 0.01 | A |  |  | R | IV curve sweep current 20
| 136C | IVCurve_Voltage21 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 21
| 136D | IVCurve_Current21 | U16 | 0.01 | A |  |  | R | IV curve sweep current 21
| 136E | IVCurve_Voltage22 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 22
| 136F | IVCurve_Current22 | U16 | 0.01 | A |  |  | R | IV curve sweep current 22
| 1370 | IVCurve_Voltage23 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 23
| 1371 | IVCurve_Current23 | U16 | 0.01 | A |  |  | R | IV curve sweep current 23
| 1372 | IVCurve_Voltage24 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 24
| 1373 | IVCurve_Current24 | U16 | 0.01 | A |  |  | R | IV curve sweep current 24
| 1374 | IVCurve_Voltage25 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 25
| 1375 | IVCurve_Current25 | U16 | 0.01 | A |  |  | R | IV curve sweep current 25
| 1376 | IVCurve_Voltage26 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 26
| 1377 | IVCurve_Current26 | U16 | 0.01 | A |  |  | R | IV curve sweep current 26
| 1378 | IVCurve_Voltage27 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 27
| 1379 | IVCurve_Current27 | U16 | 0.01 | A |  |  | R | IV curve sweep current 27
| 137A | IVCurve_Voltage28 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 28
| 137B | IVCurve_Current28 | U16 | 0.01 | A |  |  | R | IV curve sweep current 28
| 137C | IVCurve_Voltage29 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 29
| 137D | IVCurve_Current29 | U16 | 0.01 | A |  |  | R | IV curve sweep current 29
| 137E | IVCurve_Voltage30 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 30
| 137F | IVCurve_Current30 | U16 | 0.01 | A |  |  | R | IV curve sweep current 30
| 1380 | AddressMask_Config_ReadOnly_Result3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
1381
1382
1383
| 1384 | IVCurve_Voltage31 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 31
| 1385 | IVCurve_Current31 | U16 | 0.01 | A |  |  | R | IV curve sweep current 31
| 1386 | IVCurve_Voltage32 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 32
| 1387 | IVCurve_Current32 | U16 | 0.01 | A |  |  | R | IV curve sweep current 32
| 1388 | IVCurve_Voltage33 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 33
| 1389 | IVCurve_Current33 | U16 | 0.01 | A |  |  | R | IV curve sweep current 33
| 138A | IVCurve_Voltage34 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 34
| 138B | IVCurve_Current34 | U16 | 0.01 | A |  |  | R | IV curve sweep current 34
| 138C | IVCurve_Voltage35 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 35
| 138D | IVCurve_Current35 | U16 | 0.01 | A |  |  | R | IV curve sweep current 35
| 138E | IVCurve_Voltage36 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 36
| 138F | IVCurve_Current36 | U16 | 0.01 | A |  |  | R | IV curve sweep current 36
| 1390 | IVCurve_Voltage37 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 37
| 1391 | IVCurve_Current37 | U16 | 0.01 | A |  |  | R | IV curve sweep current 37
| 1392 | IVCurve_Voltage38 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 38
| 1393 | IVCurve_Current38 | U16 | 0.01 | A |  |  | R | IV curve sweep current 38
| 1394 | IVCurve_Voltage39 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 39
| 1395 | IVCurve_Current39 | U16 | 0.01 | A |  |  | R | IV curve sweep current 39
| 1396 | IVCurve_Voltage40 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 40
| 1397 | IVCurve_Current40 | U16 | 0.01 | A |  |  | R | IV curve sweep current 40
| 1398 | IVCurve_Voltage41 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 41
| 1399 | IVCurve_Current41 | U16 | 0.01 | A |  |  | R | IV curve sweep current 41
| 139A | IVCurve_Voltage42 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 42
| 139B | IVCurve_Current42 | U16 | 0.01 | A |  |  | R | IV curve sweep current 42
| 139C | IVCurve_Voltage43 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 43
| 139D | IVCurve_Current43 | U16 | 0.01 | A |  |  | R | IV curve sweep current 43
| 139E | IVCurve_Voltage44 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 44
| 139F | IVCurve_Current44 | U16 | 0.01 | A |  |  | R | IV curve sweep current 44
| 13A0 | IVCurve_Voltage45 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 45
| 13A1 | IVCurve_Current45 | U16 | 0.01 | A |  |  | R | IV curve sweep current 45
| 13A2 | IVCurve_Voltage46 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 46
| 13A3 | IVCurve_Current46 | U16 | 0.01 | A |  |  | R | IV curve sweep current 46
| 13A4 | IVCurve_Voltage47 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 47
| 13A5 | IVCurve_Current47 | U16 | 0.01 | A |  |  | R | IV curve sweep current 47
| 13A6 | IVCurve_Voltage48 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 48
| 13A7 | IVCurve_Current48 | U16 | 0.01 | A |  |  | R | IV curve sweep current 48
| 13A8 | IVCurve_Voltage49 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 49
| 13A9 | IVCurve_Current49 | U16 | 0.01 | A |  |  | R | IV curve sweep current 49
| 13AA | IVCurve_Voltage50 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 50
| 13AB | IVCurve_Current50 | U16 | 0.01 | A |  |  | R | IV curve sweep current 50
| 13AC | IVCurve_Voltage51 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 51
| 13AD | IVCurve_Current51 | U16 | 0.01 | A |  |  | R | IV curve sweep current 51
| 13AE | IVCurve_Voltage52 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 52
| 13AF | IVCurve_Current52 | U16 | 0.01 | A |  |  | R | IV curve sweep current 52
| 13B0 | IVCurve_Voltage53 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 53
| 13B1 | IVCurve_Current53 | U16 | 0.01 | A |  |  | R | IV curve sweep current 53
| 13B2 | IVCurve_Voltage54 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 54
| 13B3 | IVCurve_Current54 | U16 | 0.01 | A |  |  | R | IV curve sweep current 54
| 13B4 | IVCurve_Voltage55 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 55
| 13B5 | IVCurve_Current55 | U16 | 0.01 | A |  |  | R | IV curve sweep current 55
| 13B6 | IVCurve_Voltage56 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 56
| 13B7 | IVCurve_Current56 | U16 | 0.01 | A |  |  | R | IV curve sweep current 56
| 13B8 | IVCurve_Voltage57 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 57
| 13B9 | IVCurve_Current57 | U16 | 0.01 | A |  |  | R | IV curve sweep current 57
| 13BA | IVCurve_Voltage58 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 58
| 13BB | IVCurve_Current58 | U16 | 0.01 | A |  |  | R | IV curve sweep current 58
| 13BC | IVCurve_Voltage59 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 59
| 13BD | IVCurve_Current59 | U16 | 0.01 | A |  |  | R | IV curve sweep current 59
| 13BE | IVCurve_Voltage60 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 60
| 13BF | IVCurve_Current60 | U16 | 0.01 | A |  |  | R | IV curve sweep current 60
| 13C0 | AddressMask_Config_ReadOnly_Result4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
13C1
13C2
13C3
| 13C4 | IVCurve_Voltage61 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 61
| 13C5 | IVCurve_Current61 | U16 | 0.01 | A |  |  | R | IV curve sweep current 61
| 13C6 | IVCurve_Voltage62 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 62
| 13C7 | IVCurve_Current62 | U16 | 0.01 | A |  |  | R | IV curve sweep current 62
| 13C8 | IVCurve_Voltage63 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 63
| 13C9 | IVCurve_Current63 | U16 | 0.01 | A |  |  | R | IV curve sweep current 63
| 13CA | IVCurve_Voltage64 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 64
| 13CB | IVCurve_Current64 | U16 | 0.01 | A |  |  | R | IV curve sweep current 64
| 13CC | IVCurve_Voltage65 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 65
| 13CD | IVCurve_Current65 | U16 | 0.01 | A |  |  | R | IV curve sweep current 65
| 13CE | IVCurve_Voltage66 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 66
| 13CF | IVCurve_Current66 | U16 | 0.01 | A |  |  | R | IV curve sweep current 66
| 13D0 | IVCurve_Voltage67 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 67
| 13D1 | IVCurve_Current67 | U16 | 0.01 | A |  |  | R | IV curve sweep current 67
| 13D2 | IVCurve_Voltage68 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 68
| 13D3 | IVCurve_Current68 | U16 | 0.01 | A |  |  | R | IV curve sweep current 68
| 13D4 | IVCurve_Voltage69 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 69
| 13D5 | IVCurve_Current69 | U16 | 0.01 | A |  |  | R | IV curve sweep current 69
| 13D6 | IVCurve_Voltage70 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 70
| 13D7 | IVCurve_Current70 | U16 | 0.01 | A |  |  | R | IV curve sweep current 70
| 13D8 | IVCurve_Voltage71 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 71
| 13D9 | IVCurve_Current71 | U16 | 0.01 | A |  |  | R | IV curve sweep current 71
| 13DA | IVCurve_Voltage72 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 72
| 13DB | IVCurve_Current72 | U16 | 0.01 | A |  |  | R | IV curve sweep current 72
| 13DC | IVCurve_Voltage73 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 73
| 13DD | IVCurve_Current73 | U16 | 0.01 | A |  |  | R | IV curve sweep current 73
| 13DE | IVCurve_Voltage74 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 74
| 13DF | IVCurve_Current74 | U16 | 0.01 | A |  |  | R | IV curve sweep current 74
| 13E0 | IVCurve_Voltage75 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 75
| 13E1 | IVCurve_Current75 | U16 | 0.01 | A |  |  | R | IV curve sweep current 75
| 13E2 | IVCurve_Voltage76 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 76
| 13E3 | IVCurve_Current76 | U16 | 0.01 | A |  |  | R | IV curve sweep current 76
| 13E4 | IVCurve_Voltage77 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 77
| 13E5 | IVCurve_Current77 | U16 | 0.01 | A |  |  | R | IV curve sweep current 77
| 13E6 | IVCurve_Voltage78 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 78
| 13E7 | IVCurve_Current78 | U16 | 0.01 | A |  |  | R | IV curve sweep current 78
| 13E8 | IVCurve_Voltage79 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 79
| 13E9 | IVCurve_Current79 | U16 | 0.01 | A |  |  | R | IV curve sweep current 79
| 13EA | IVCurve_Voltage80 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 80
| 13EB | IVCurve_Current80 | U16 | 0.01 | A |  |  | R | IV curve sweep current 80
| 13EC | IVCurve_Voltage81 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 81
| 13ED | IVCurve_Current81 | U16 | 0.01 | A |  |  | R | IV curve sweep current 81
| 13EE | IVCurve_Voltage82 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 82
| 13EF | IVCurve_Current82 | U16 | 0.01 | A |  |  | R | IV curve sweep current 82
| 13F0 | IVCurve_Voltage83 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 83
| 13F1 | IVCurve_Current83 | U16 | 0.01 | A |  |  | R | IV curve sweep current 83
| 13F2 | IVCurve_Voltage84 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 84
| 13F3 | IVCurve_Current84 | U16 | 0.01 | A |  |  | R | IV curve sweep current 84
| 13F4 | IVCurve_Voltage85 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 85
| 13F5 | IVCurve_Current85 | U16 | 0.01 | A |  |  | R | IV curve sweep current 85
| 13F6 | IVCurve_Voltage86 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 86
| 13F7 | IVCurve_Current86 | U16 | 0.01 | A |  |  | R | IV curve sweep current 86
| 13F8 | IVCurve_Voltage87 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 87
| 13F9 | IVCurve_Current87 | U16 | 0.01 | A |  |  | R | IV curve sweep current 87
| 13FA | IVCurve_Voltage88 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 88
| 13FB | IVCurve_Current88 | U16 | 0.01 | A |  |  | R | IV curve sweep current 88
| 13FC | IVCurve_Voltage89 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 89
| 13FD | IVCurve_Current89 | U16 | 0.01 | A |  |  | R | IV curve sweep current 89
| 13FE | IVCurve_Voltage90 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 90
| 13FF | IVCurve_Current90 | U16 | 0.01 | A |  |  | R | IV curve sweep current 90
| 1400 | AddressMask_Config_ReadOnly_Result5 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
1401
1402
1403
| 1404 | IVCurve_Voltage91 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 91
| 1405 | IVCurve_Current91 | U16 | 0.01 | A |  |  | R | IV curve sweep current 91
| 1406 | IVCurve_Voltage92 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 92
| 1407 | IVCurve_Current92 | U16 | 0.01 | A |  |  | R | IV curve sweep current 92
| 1408 | IVCurve_Voltage93 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 93
| 1409 | IVCurve_Current93 | U16 | 0.01 | A |  |  | R | IV curve sweep current 93
| 140A | IVCurve_Voltage94 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 94
| 140B | IVCurve_Current94 | U16 | 0.01 | A |  |  | R | IV curve sweep current 94
| 140C | IVCurve_Voltage95 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 95
| 140D | IVCurve_Current95 | U16 | 0.01 | A |  |  | R | IV curve sweep current 95
| 140E | IVCurve_Voltage96 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 96
| 140F | IVCurve_Current96 | U16 | 0.01 | A |  |  | R | IV curve sweep current 96
| 1410 | IVCurve_Voltage97 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 97
| 1411 | IVCurve_Current97 | U16 | 0.01 | A |  |  | R | IV curve sweep current 97
| 1412 | IVCurve_Voltage98 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 98
| 1413 | IVCurve_Current98 | U16 | 0.01 | A |  |  | R | IV curve sweep current 98
| 1414 | IVCurve_Voltage99 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 99
| 1415 | IVCurve_Current99 | U16 | 0.01 | A |  |  | R | IV curve sweep current 99
| 1416 | IVCurve_Voltage100 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 100
| 1417 | IVCurve_Current100 | U16 | 0.01 | A |  |  | R | IV curve sweep current 100
| 1418 | IVCurve_Voltage101 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 101
| 1419 | IVCurve_Current101 | U16 | 0.01 | A |  |  | R | IV curve sweep current 101
| 141A | IVCurve_Voltage102 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 102
| 141B | IVCurve_Current102 | U16 | 0.01 | A |  |  | R | IV curve sweep current 102
| 141C | IVCurve_Voltage103 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 103
| 141D | IVCurve_Current103 | U16 | 0.01 | A |  |  | R | IV curve sweep current 103
| 141E | IVCurve_Voltage104 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 104
| 141F | IVCurve_Current104 | U16 | 0.01 | A |  |  | R | IV curve sweep current 104
| 1420 | IVCurve_Voltage105 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 105
| 1421 | IVCurve_Current105 | U16 | 0.01 | A |  |  | R | IV curve sweep current 105
| 1422 | IVCurve_Voltage106 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 106
| 1423 | IVCurve_Current106 | U16 | 0.01 | A |  |  | R | IV curve sweep current 106
| 1424 | IVCurve_Voltage107 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 107
| 1425 | IVCurve_Current107 | U16 | 0.01 | A |  |  | R | IV curve sweep current 107
| 1426 | IVCurve_Voltage108 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 108
| 1427 | IVCurve_Current108 | U16 | 0.01 | A |  |  | R | IV curve sweep current 108
| 1428 | IVCurve_Voltage109 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 109
| 1429 | IVCurve_Current109 | U16 | 0.01 | A |  |  | R | IV curve sweep current 109
| 142A | IVCurve_Voltage110 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 110
| 142B | IVCurve_Current110 | U16 | 0.01 | A |  |  | R | IV curve sweep current 110
| 142C | IVCurve_Voltage111 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 111
| 142D | IVCurve_Current111 | U16 | 0.01 | A |  |  | R | IV curve sweep current 111
| 142E | IVCurve_Voltage112 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 112
| 142F | IVCurve_Current112 | U16 | 0.01 | A |  |  | R | IV curve sweep current 112
| 1430 | IVCurve_Voltage113 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 113
| 1431 | IVCurve_Current113 | U16 | 0.01 | A |  |  | R | IV curve sweep current 113
| 1432 | IVCurve_Voltage114 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 114
| 1433 | IVCurve_Current114 | U16 | 0.01 | A |  |  | R | IV curve sweep current 114
| 1434 | IVCurve_Voltage115 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 115
| 1435 | IVCurve_Current115 | U16 | 0.01 | A |  |  | R | IV curve sweep current 115
| 1436 | IVCurve_Voltage116 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 116
| 1437 | IVCurve_Current116 | U16 | 0.01 | A |  |  | R | IV curve sweep current 116
| 1438 | IVCurve_Voltage117 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 117
| 1439 | IVCurve_Current117 | U16 | 0.01 | A |  |  | R | IV curve sweep current 117
| 143A | IVCurve_Voltage118 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 118
| 143B | IVCurve_Current118 | U16 | 0.01 | A |  |  | R | IV curve sweep current 118
| 143C | IVCurve_Voltage119 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 119
| 143D | IVCurve_Current119 | U16 | 0.01 | A |  |  | R | IV curve sweep current 119
| 143E | IVCurve_Voltage120 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 120
| 143F | IVCurve_Current120 | U16 | 0.01 | A |  |  | R | IV curve sweep current 120
| 1440 | AddressMask_Config_ReadOnly_Result6 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
1441
1442
1443
| 1444 | IVCurve_Voltage121 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 121
| 1445 | IVCurve_Current121 | U16 | 0.01 | A |  |  | R | IV curve sweep current 121
| 1446 | IVCurve_Voltage122 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 122
| 1447 | IVCurve_Current122 | U16 | 0.01 | A |  |  | R | IV curve sweep current 122
| 1448 | IVCurve_Voltage123 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 123
| 1449 | IVCurve_Current123 | U16 | 0.01 | A |  |  | R | IV curve sweep current 123
| 144A | IVCurve_Voltage124 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 124
| 144B | IVCurve_Current124 | U16 | 0.01 | A |  |  | R | IV curve sweep current 124
| 144C | IVCurve_Voltage125 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 125
| 144D | IVCurve_Current125 | U16 | 0.01 | A |  |  | R | IV curve sweep current 125
| 144E | IVCurve_Voltage126 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 126
| 144F | IVCurve_Current126 | U16 | 0.01 | A |  |  | R | IV curve sweep current 126
| 1450 | IVCurve_Voltage127 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 127
| 1451 | IVCurve_Current127 | U16 | 0.01 | A |  |  | R | IV curve sweep current 127
| 1452 | IVCurve_Voltage128 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 128
| 1453 | IVCurve_Current128 | U16 | 0.01 | A |  |  | R | IV curve sweep current 128
| 1454 | IVCurve_Voltage129 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 129
| 1455 | IVCurve_Current129 | U16 | 0.01 | A |  |  | R | IV curve sweep current 129
| 1456 | IVCurve_Voltage130 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 130
| 1457 | IVCurve_Current130 | U16 | 0.01 | A |  |  | R | IV curve sweep current 130
| 1458 | IVCurve_Voltage131 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 131
| 1459 | IVCurve_Current131 | U16 | 0.01 | A |  |  | R | IV curve sweep current 131
| 145A | IVCurve_Voltage132 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 132
| 145B | IVCurve_Current132 | U16 | 0.01 | A |  |  | R | IV curve sweep current 132
| 145C | IVCurve_Voltage133 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 133
| 145D | IVCurve_Current133 | U16 | 0.01 | A |  |  | R | IV curve sweep current 133
| 145E | IVCurve_Voltage134 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 134
| 145F | IVCurve_Current134 | U16 | 0.01 | A |  |  | R | IV curve sweep current 134
| 1460 | IVCurve_Voltage135 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 135
| 1461 | IVCurve_Current135 | U16 | 0.01 | A |  |  | R | IV curve sweep current 135
| 1462 | IVCurve_Voltage136 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 136
| 1463 | IVCurve_Current136 | U16 | 0.01 | A |  |  | R | IV curve sweep current 136
| 1464 | IVCurve_Voltage137 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 137
| 1465 | IVCurve_Current137 | U16 | 0.01 | A |  |  | R | IV curve sweep current 137
| 1466 | IVCurve_Voltage138 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 138
| 1467 | IVCurve_Current138 | U16 | 0.01 | A |  |  | R | IV curve sweep current 138
| 1468 | IVCurve_Voltage139 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 139
| 1469 | IVCurve_Current139 | U16 | 0.01 | A |  |  | R | IV curve sweep current 139
| 146A | IVCurve_Voltage140 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 140
| 146B | IVCurve_Current140 | U16 | 0.01 | A |  |  | R | IV curve sweep current 140
| 146C | IVCurve_Voltage141 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 141
| 146D | IVCurve_Current141 | U16 | 0.01 | A |  |  | R | IV curve sweep current 141
| 146E | IVCurve_Voltage142 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 142
| 146F | IVCurve_Current142 | U16 | 0.01 | A |  |  | R | IV curve sweep current 142
| 1470 | IVCurve_Voltage143 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 143
| 1471 | IVCurve_Current143 | U16 | 0.01 | A |  |  | R | IV curve sweep current 143
| 1472 | IVCurve_Voltage144 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 144
| 1473 | IVCurve_Current144 | U16 | 0.01 | A |  |  | R | IV curve sweep current 144
| 1474 | IVCurve_Voltage145 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 145
| 1475 | IVCurve_Current145 | U16 | 0.01 | A |  |  | R | IV curve sweep current 145
| 1476 | IVCurve_Voltage146 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 146
| 1477 | IVCurve_Current146 | U16 | 0.01 | A |  |  | R | IV curve sweep current 146
| 1478 | IVCurve_Voltage147 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 147
| 1479 | IVCurve_Current147 | U16 | 0.01 | A |  |  | R | IV curve sweep current 147
| 147A | IVCurve_Voltage148 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 148
| 147B | IVCurve_Current148 | U16 | 0.01 | A |  |  | R | IV curve sweep current 148
| 147C | IVCurve_Voltage149 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 149
| 147D | IVCurve_Current149 | U16 | 0.01 | A |  |  | R | IV curve sweep current 149
| 147E | IVCurve_Voltage150 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 150
| 147F | IVCurve_Current150 | U16 | 0.01 | A |  |  | R | IV curve scan current 150
| 1480 | HistoryEventList_ID1 | U16 |  |  |  |  | R | History Event ID Last 1st entry
| 1481 | HistoryEventList_yM1 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1482 | HistoryEventList_dH1 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1483 | HistoryEventList_ms1 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1484 | HistoryEventList_ID2 | U16 |  |  |  |  | R | History Event ID Last 2nd entry
| 1485 | HistoryEventList_yM2 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1486 | HistoryEventList_dH2 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1487 | HistoryEventList_ms2 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1488 | HistoryEventList_ID3 | U16 |  |  |  |  | R | History event ID last 3rd entry
| 1489 | HistoryEventList_yM3 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 148A | HistoryEventList_dH3 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 148B | HistoryEventList_ms3 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 148C | HistoryEventList_ID4 | U16 |  |  |  |  | R | History Event ID Last 4th entry
| 148D | HistoryEventList_yM4 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 148E | HistoryEventList_dH4 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 148F | HistoryEventList_ms4 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1490 | HistoryEventList_ID5 | U16 |  |  |  |  | R | History Event ID Last 5th entry
| 1491 | HistoryEventList_yM5 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1492 | HistoryEventList_dH5 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1493 | HistoryEventList_ms5 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1494 | HistoryEventList_ID6 | U16 |  |  |  |  | R | History Event ID Most Recent Article 6
| 1495 | HistoryEventList_yM6 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1496 | HistoryEventList_dH6 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1497 | HistoryEventList_ms6 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1498 | HistoryEventList_ID7 | U16 |  |  |  |  | R | History Event ID Last Article 7
| 1499 | HistoryEventList_yM7 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 149A | HistoryEventList_dH7 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 149B | HistoryEventList_ms7 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 149C | HistoryEventList_ID8 | U16 |  |  |  |  | R | History Event ID Last 8th entry
| 149D | HistoryEventList_yM8 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 149E | HistoryEventList_dH8 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 149F | HistoryEventList_ms8 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14A0 | HistoryEventList_ID9 | U16 |  |  |  |  | R | History Event ID last 9th entry
| 14A1 | HistoryEventList_yM9 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14A2 | HistoryEventList_dH9 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14A3 | HistoryEventList_ms9 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14A4 | HistoryEventList_ID10 | U16 |  |  |  |  | R | History Event ID Last 10th entry
| 14A5 | HistoryEventList_yM10 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14A6 | HistoryEventList_dH10 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14A7 | HistoryEventList_ms10 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14A8 | HistoryEventList_ID11 | U16 |  |  |  |  | R | History Event ID Recent 11th entry
| 14A9 | HistoryEventList_yM11 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14AA | HistoryEventList_dH11 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14AB | HistoryEventList_ms11 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14AC | HistoryEventList_ID12 | U16 |  |  |  |  | R | History Event ID Last 12th entry
| 14AD | HistoryEventList_yM12 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14AE | HistoryEventList_dH12 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14AF | HistoryEventList_ms12 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14B0 | HistoryEventList_ID13 | U16 |  |  |  |  | R | History Event ID Last Article 13
| 14B1 | HistoryEventList_yM13 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14B2 | HistoryEventList_dH13 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14B3 | HistoryEventList_ms13 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14B4 | HistoryEventList_ID14 | U16 |  |  |  |  | R | History Event ID Last Article 14
| 14B5 | HistoryEventList_yM14 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14B6 | HistoryEventList_dH14 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14B7 | HistoryEventList_ms14 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14B8 | HistoryEventList_ID15 | U16 |  |  |  |  | R | History Event ID last 15th entry
| 14B9 | HistoryEventList_yM15 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14BA | HistoryEventList_dH15 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14BB | HistoryEventList_ms15 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14BC | HistoryEventList_ID16 | U16 |  |  |  |  | R | History Event ID Last Article 16
| 14BD | HistoryEventList_yM16 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14BE | HistoryEventList_dH16 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14BF | HistoryEventList_ms16 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14C0 | HistoryEventList_ID17 | U16 |  |  |  |  | R | History Event ID Last Article 17
| 14C1 | HistoryEventList_yM17 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14C2 | HistoryEventList_dH17 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14C3 | HistoryEventList_ms17 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14C4 | HistoryEventList_ID18 | U16 |  |  |  |  | R | History Event ID Last Article 18
| 14C5 | HistoryEventList_yM18 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14C6 | HistoryEventList_dH18 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14C7 | HistoryEventList_ms18 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14C8 | HistoryEventList_ID19 | U16 |  |  |  |  | R | History Event ID Last Article 19
| 14C9 | HistoryEventList_yM19 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14CA | HistoryEventList_dH19 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14CB | HistoryEventList_ms19 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14CC | HistoryEventList_ID20 | U16 |  |  |  |  | R | History Event ID last 20th entry
| 14CD | HistoryEventList_yM20 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14CE | HistoryEventList_dH20 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14CF | HistoryEventList_ms20 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14D0 | HistoryEventList_ID21 | U16 |  |  |  |  | R | History Event ID Last Article 21
| 14D1 | HistoryEventList_yM21 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14D2 | HistoryEventList_dH21 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14D3 | HistoryEventList_ms21 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14D4 | HistoryEventList_ID22 | U16 |  |  |  |  | R | History Event ID Last Article 22
| 14D5 | HistoryEventList_yM22 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14D6 | HistoryEventList_dH22 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14D7 | HistoryEventList_ms22 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14D8 | HistoryEventList_ID23 | U16 |  |  |  |  | R | History Event ID Last Article 23
| 14D9 | HistoryEventList_yM23 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14DA | HistoryEventList_dH23 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14DB | HistoryEventList_ms23 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14DC | HistoryEventList_ID24 | U16 |  |  |  |  | R | History Event ID Last Article 24
| 14DD | HistoryEventList_yM24 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14DE | HistoryEventList_dH24 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14DF | HistoryEventList_ms24 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14E0 | HistoryEventList_ID25 | U16 |  |  |  |  | R | History Event ID Last Article 25
| 14E1 | HistoryEventList_yM25 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14E2 | HistoryEventList_dH25 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14E3 | HistoryEventList_ms25 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14E4 | HistoryEventList_ID26 | U16 |  |  |  |  | R | History Event ID Last Article 26
| 14E5 | HistoryEventList_yM26 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14E6 | HistoryEventList_dH26 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14E7 | HistoryEventList_ms26 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14E8 | HistoryEventList_ID27 | U16 |  |  |  |  | R | History Event ID Last Article 27
| 14E9 | HistoryEventList_yM27 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14EA | HistoryEventList_dH27 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14EB | HistoryEventList_ms27 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14EC | HistoryEventList_ID28 | U16 |  |  |  |  | R | History Event ID Last Article 28
| 14ED | HistoryEventList_yM28 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14EE | HistoryEventList_dH28 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14EF | HistoryEventList_ms28 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14F0 | HistoryEventList_ID29 | U16 |  |  |  |  | R | History Event ID Last Article 29
| 14F1 | HistoryEventList_yM29 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14F2 | HistoryEventList_dH29 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14F3 | HistoryEventList_ms29 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14F4 | HistoryEventList_ID30 | U16 |  |  |  |  | R | History Event ID last 30th entry
| 14F5 | HistoryEventList_yM30 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14F6 | HistoryEventList_dH30 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14F7 | HistoryEventList_ms30 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14F8 | HistoryEventList_ID31 | U16 |  |  |  |  | R | History Event ID Last Article 31
| 14F9 | HistoryEventList_yM31 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14FA | HistoryEventList_dH31 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14FB | HistoryEventList_ms31 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 14FC | HistoryEventList_ID32 | U16 |  |  |  |  | R | History Event ID Last Article 32
| 14FD | HistoryEventList_yM32 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 14FE | HistoryEventList_dH32 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 14FF | HistoryEventList_ms32 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1500 | HistoryEventList_ID33 | U16 |  |  |  |  | R | History Event ID Last Article 33
| 1501 | HistoryEventList_yM33 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1502 | HistoryEventList_dH33 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1503 | HistoryEventList_ms33 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1504 | HistoryEventList_ID34 | U16 |  |  |  |  | R | History Event ID Last Article 34
| 1505 | HistoryEventList_yM34 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1506 | HistoryEventList_dH34 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1507 | HistoryEventList_ms34 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1508 | HistoryEventList_ID35 | U16 |  |  |  |  | R | History Event ID Last Article 35
| 1509 | HistoryEventList_yM35 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 150A | HistoryEventList_dH35 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 150B | HistoryEventList_ms35 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 150C | HistoryEventList_ID36 | U16 |  |  |  |  | R | History Event ID Last Article 36
| 150D | HistoryEventList_yM36 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 150E | HistoryEventList_dH36 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 150F | HistoryEventList_ms36 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1510 | HistoryEventList_ID37 | U16 |  |  |  |  | R | History Event ID Last Article 37
| 1511 | HistoryEventList_yM37 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1512 | HistoryEventList_dH37 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1513 | HistoryEventList_ms37 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1514 | HistoryEventList_ID38 | U16 |  |  |  |  | R | History Event ID Last Article 38
| 1515 | HistoryEventList_yM38 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1516 | HistoryEventList_dH38 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1517 | HistoryEventList_ms38 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1518 | HistoryEventList_ID39 | U16 |  |  |  |  | R | History Event ID Last Article 39
| 1519 | HistoryEventList_yM39 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 151A | HistoryEventList_dH39 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 151B | HistoryEventList_ms39 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 151C | HistoryEventList_ID40 | U16 |  |  |  |  | R | History Event ID Last Article 40
| 151D | HistoryEventList_yM40 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 151E | HistoryEventList_dH40 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 151F | HistoryEventList_ms40 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1520 | HistoryEventList_ID41 | U16 |  |  |  |  | R | History Event ID Last Article 41
| 1521 | HistoryEventList_yM41 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1522 | HistoryEventList_dH41 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1523 | HistoryEventList_ms41 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1524 | HistoryEventList_ID42 | U16 |  |  |  |  | R | History Event ID Last Article 42
| 1525 | HistoryEventList_yM42 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1526 | HistoryEventList_dH42 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1527 | HistoryEventList_ms42 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1528 | HistoryEventList_ID43 | U16 |  |  |  |  | R | History Event ID Last Article 43
| 1529 | HistoryEventList_yM43 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 152A | HistoryEventList_dH43 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 152B | HistoryEventList_ms43 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 152C | HistoryEventList_ID44 | U16 |  |  |  |  | R | History Event ID Last Article 44
| 152D | HistoryEventList_yM44 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 152E | HistoryEventList_dH44 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 152F | HistoryEventList_ms44 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1530 | HistoryEventList_ID45 | U16 |  |  |  |  | R | History Event ID Last Article 45
| 1531 | HistoryEventList_yM45 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1532 | HistoryEventList_dH45 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1533 | HistoryEventList_ms45 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1534 | HistoryEventList_ID46 | U16 |  |  |  |  | R | Historical Event ID Last Article 46
| 1535 | HistoryEventList_yM46 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1536 | HistoryEventList_dH46 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1537 | HistoryEventList_ms46 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1538 | HistoryEventList_ID47 | U16 |  |  |  |  | R | History Event ID Last Article 47
| 1539 | HistoryEventList_yM47 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 153A | HistoryEventList_dH47 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 153B | HistoryEventList_ms47 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 153C | HistoryEventList_ID48 | U16 |  |  |  |  | R | History Event ID Last Article 48
| 153D | HistoryEventList_yM48 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 153E | HistoryEventList_dH48 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 153F | HistoryEventList_ms48 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1540 | HistoryEventList_ID49 | U16 |  |  |  |  | R | History Event ID Last Article 49
| 1541 | HistoryEventList_yM49 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1542 | HistoryEventList_dH49 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1543 | HistoryEventList_ms49 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1544 | HistoryEventList_ID50 | U16 |  |  |  |  | R | History Event ID last 50th entry
| 1545 | HistoryEventList_yM50 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1546 | HistoryEventList_dH50 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1547 | HistoryEventList_ms50 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1548 | HistoryEventList_ID51 | U16 |  |  |  |  | R | History Event ID Last Article 51
| 1549 | HistoryEventList_yM51 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 154A | HistoryEventList_dH51 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 154B | HistoryEventList_ms51 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 154C | HistoryEventList_ID52 | U16 |  |  |  |  | R | History Event ID Last Article 52
| 154D | HistoryEventList_yM52 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 154E | HistoryEventList_dH52 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 154F | HistoryEventList_ms52 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1550 | HistoryEventList_ID53 | U16 |  |  |  |  | R | Historical Event ID Last Article 53
| 1551 | HistoryEventList_yM53 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1552 | HistoryEventList_dH53 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1553 | HistoryEventList_ms53 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1554 | HistoryEventList_ID54 | U16 |  |  |  |  | R | Historical Event ID Last Article 54
| 1555 | HistoryEventList_yM54 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1556 | HistoryEventList_dH54 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1557 | HistoryEventList_ms54 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1558 | HistoryEventList_ID55 | U16 |  |  |  |  | R | History Event ID Last Article 55
| 1559 | HistoryEventList_yM55 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 155A | HistoryEventList_dH55 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 155B | HistoryEventList_ms55 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 155C | HistoryEventList_ID56 | U16 |  |  |  |  | R | History Event ID Last Article 56
| 155D | HistoryEventList_yM56 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 155E | HistoryEventList_dH56 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 155F | HistoryEventList_ms56 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1560 | HistoryEventList_ID57 | U16 |  |  |  |  | R | History Event ID Recent Article 57
| 1561 | HistoryEventList_yM57 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1562 | HistoryEventList_dH57 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1563 | HistoryEventList_ms57 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1564 | HistoryEventList_ID58 | U16 |  |  |  |  | R | History Event ID Last Article 58
| 1565 | HistoryEventList_yM58 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1566 | HistoryEventList_dH58 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1567 | HistoryEventList_ms58 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1568 | HistoryEventList_ID59 | U16 |  |  |  |  | R | History Event ID Last Article 59
| 1569 | HistoryEventList_yM59 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 156A | HistoryEventList_dH59 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 156B | HistoryEventList_ms59 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 156C | HistoryEventList_ID60 | U16 |  |  |  |  | R | History Event ID Last Article 60
| 156D | HistoryEventList_yM60 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 156E | HistoryEventList_dH60 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 156F | HistoryEventList_ms60 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1570 | HistoryEventList_ID61 | U16 |  |  |  |  | R | History Event ID Recent Article 61
| 1571 | HistoryEventList_yM61 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1572 | HistoryEventList_dH61 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1573 | HistoryEventList_ms61 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1574 | HistoryEventList_ID62 | U16 |  |  |  |  | R | History Event ID Last Article 62
| 1575 | HistoryEventList_yM62 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1576 | HistoryEventList_dH62 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1577 | HistoryEventList_ms62 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1578 | HistoryEventList_ID63 | U16 |  |  |  |  | R | History Event ID Recent Article 63
| 1579 | HistoryEventList_yM63 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 157A | HistoryEventList_dH63 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 157B | HistoryEventList_ms63 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 157C | HistoryEventList_ID64 | U16 |  |  |  |  | R | History Event ID Recent Article 64
| 157D | HistoryEventList_yM64 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 157E | HistoryEventList_dH64 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 157F | HistoryEventList_ms64 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1580 | HistoryEventList_ID65 | U16 |  |  |  |  | R | History Event ID Last Article 65
| 1581 | HistoryEventList_yM65 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1582 | HistoryEventList_dH65 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1583 | HistoryEventList_ms65 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1584 | HistoryEventList_ID66 | U16 |  |  |  |  | R | History Event ID Recent Article 66
| 1585 | HistoryEventList_yM66 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1586 | HistoryEventList_dH66 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1587 | HistoryEventList_ms66 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1588 | HistoryEventList_ID67 | U16 |  |  |  |  | R | History Event ID Recent Article 67
| 1589 | HistoryEventList_yM67 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 158A | HistoryEventList_dH67 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 158B | HistoryEventList_ms67 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 158C | HistoryEventList_ID68 | U16 |  |  |  |  | R | Historical Event ID Recent Article 68
| 158D | HistoryEventList_yM68 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 158E | HistoryEventList_dH68 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 158F | HistoryEventList_ms68 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1590 | HistoryEventList_ID69 | U16 |  |  |  |  | R | History Event ID Recent Article 69
| 1591 | HistoryEventList_yM69 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1592 | HistoryEventList_dH69 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1593 | HistoryEventList_ms69 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1594 | HistoryEventList_ID70 | U16 |  |  |  |  | R | History Event ID Last Article 70
| 1595 | HistoryEventList_yM70 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1596 | HistoryEventList_dH70 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1597 | HistoryEventList_ms70 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1598 | HistoryEventList_ID71 | U16 |  |  |  |  | R | History Event ID Recent Article 71
| 1599 | HistoryEventList_yM71 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 159A | HistoryEventList_dH71 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 159B | HistoryEventList_ms71 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 159C | HistoryEventList_ID72 | U16 |  |  |  |  | R | History Event ID Last Article 72
| 159D | HistoryEventList_yM72 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 159E | HistoryEventList_dH72 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 159F | HistoryEventList_ms72 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15A0 | HistoryEventList_ID73 | U16 |  |  |  |  | R | History Event ID Recent Article 73
| 15A1 | HistoryEventList_yM73 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15A2 | HistoryEventList_dH73 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15A3 | HistoryEventList_ms73 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15A4 | HistoryEventList_ID74 | U16 |  |  |  |  | R | History Event ID Last Article 74
| 15A5 | HistoryEventList_yM74 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15A6 | HistoryEventList_dH74 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15A7 | HistoryEventList_ms74 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15A8 | HistoryEventList_ID75 | U16 |  |  |  |  | R | History Event ID Last Article 75
| 15A9 | HistoryEventList_yM75 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15AA | HistoryEventList_dH75 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15AB | HistoryEventList_ms75 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15AC | HistoryEventList_ID76 | U16 |  |  |  |  | R | History Event ID Recent Article 76
| 15AD | HistoryEventList_yM76 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15AE | HistoryEventList_dH76 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15AF | HistoryEventList_ms76 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15B0 | HistoryEventList_ID77 | U16 |  |  |  |  | R | History Event ID Recent Article 77
| 15B1 | HistoryEventList_yM77 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15B2 | HistoryEventList_dH77 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15B3 | HistoryEventList_ms77 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15B4 | HistoryEventList_ID78 | U16 |  |  |  |  | R | Historical Event ID Last Article 78
| 15B5 | HistoryEventList_yM78 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15B6 | HistoryEventList_dH78 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15B7 | HistoryEventList_ms78 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15B8 | HistoryEventList_ID79 | U16 |  |  |  |  | R | Historical Event ID Last Article 79
| 15B9 | HistoryEventList_yM79 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15BA | HistoryEventList_dH79 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15BB | HistoryEventList_ms79 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15BC | HistoryEventList_ID80 | U16 |  |  |  |  | R | History Event ID Last Article 80
| 15BD | HistoryEventList_yM80 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15BE | HistoryEventList_dH80 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15BF | HistoryEventList_ms80 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15C0 | HistoryEventList_ID81 | U16 |  |  |  |  | R | History Event ID Recent Article 81
| 15C1 | HistoryEventList_yM81 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15C2 | HistoryEventList_dH81 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15C3 | HistoryEventList_ms81 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15C4 | HistoryEventList_ID82 | U16 |  |  |  |  | R | History Event ID Last Article 82
| 15C5 | HistoryEventList_yM82 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15C6 | HistoryEventList_dH82 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15C7 | HistoryEventList_ms82 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15C8 | HistoryEventList_ID83 | U16 |  |  |  |  | R | History Event ID Recent Article 83
| 15C9 | HistoryEventList_yM83 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15CA | HistoryEventList_dH83 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15CB | HistoryEventList_ms83 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15CC | HistoryEventList_ID84 | U16 |  |  |  |  | R | History Event ID Last Article 84
| 15CD | HistoryEventList_yM84 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15CE | HistoryEventList_dH84 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15CF | HistoryEventList_ms84 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15D0 | HistoryEventList_ID85 | U16 |  |  |  |  | R | History Event ID Last Article 85
| 15D1 | HistoryEventList_yM85 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15D2 | HistoryEventList_dH85 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15D3 | HistoryEventList_ms85 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15D4 | HistoryEventList_ID86 | U16 |  |  |  |  | R | History Event ID Recent Article 86
| 15D5 | HistoryEventList_yM86 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15D6 | HistoryEventList_dH86 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15D7 | HistoryEventList_ms86 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15D8 | HistoryEventList_ID87 | U16 |  |  |  |  | R | Historical Event ID Recent Article 87
| 15D9 | HistoryEventList_yM87 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15DA | HistoryEventList_dH87 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15DB | HistoryEventList_ms87 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15DC | HistoryEventList_ID88 | U16 |  |  |  |  | R | Historical Event ID Recent Article 88
| 15DD | HistoryEventList_yM88 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15DE | HistoryEventList_dH88 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15DF | HistoryEventList_ms88 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15E0 | HistoryEventList_ID89 | U16 |  |  |  |  | R | Historical Event ID Last Article 89
| 15E1 | HistoryEventList_yM89 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15E2 | HistoryEventList_dH89 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15E3 | HistoryEventList_ms89 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15E4 | HistoryEventList_ID90 | U16 |  |  |  |  | R | History Event ID last 90th entry
| 15E5 | HistoryEventList_yM90 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15E6 | HistoryEventList_dH90 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15E7 | HistoryEventList_ms90 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15E8 | HistoryEventList_ID91 | U16 |  |  |  |  | R | Historical Event ID Recent Article 91
| 15E9 | HistoryEventList_yM91 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15EA | HistoryEventList_dH91 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15EB | HistoryEventList_ms91 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15EC | HistoryEventList_ID92 | U16 |  |  |  |  | R | Historical Event ID Last Article 92
| 15ED | HistoryEventList_yM92 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15EE | HistoryEventList_dH92 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15EF | HistoryEventList_ms92 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15F0 | HistoryEventList_ID93 | U16 |  |  |  |  | R | History Event ID Recent Article 93
| 15F1 | HistoryEventList_yM93 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15F2 | HistoryEventList_dH93 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15F3 | HistoryEventList_ms93 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15F4 | HistoryEventList_ID94 | U16 |  |  |  |  | R | Historical Event ID Last Article 94
| 15F5 | HistoryEventList_yM94 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15F6 | HistoryEventList_dH94 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15F7 | HistoryEventList_ms94 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15F8 | HistoryEventList_ID95 | U16 |  |  |  |  | R | History Event ID Last Article 95
| 15F9 | HistoryEventList_yM95 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15FA | HistoryEventList_dH95 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15FB | HistoryEventList_ms95 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 15FC | HistoryEventList_ID96 | U16 |  |  |  |  | R | Historical Event ID Last Article 96
| 15FD | HistoryEventList_yM96 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 15FE | HistoryEventList_dH96 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 15FF | HistoryEventList_ms96 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1600 | HistoryEventList_ID97 | U16 |  |  |  |  | R | Historical Event ID Last Article 97
| 1601 | HistoryEventList_yM97 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1602 | HistoryEventList_dH97 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1603 | HistoryEventList_ms97 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1604 | HistoryEventList_ID98 | U16 |  |  |  |  | R | Historical Event ID Last Article 98
| 1605 | HistoryEventList_yM98 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 1606 | HistoryEventList_dH98 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 1607 | HistoryEventList_ms98 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1608 | HistoryEventList_ID99 | U16 |  |  |  |  | R | Historical Event ID Last Article 99
| 1609 | HistoryEventList_yM99 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 160A | HistoryEventList_dH99 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 160B | HistoryEventList_ms99 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 160C | HistoryEventList_ID100 | U16 |  |  |  |  | R | History Event ID last 100th entry
| 160D | HistoryEventList_yM100 | U16 |  |  |  |  | R | High byte: the lower two digits of the decimal number of the year; low byte: the month.
| 160E | HistoryEventList_dH100 | U16 |  |  |  |  | R | High byte: date; low byte: hour.
| 160F | HistoryEventList_ms100 | U16 |  |  |  |  | R | High byte: minutes; low byte: seconds.
| 1610 | EnergyStatistics1 | U32 | 0.01 | kWh |  |  | R | Article 1 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1611
| 1612 | EnergyStatistics2 | U32 | 0.01 | kWh |  |  | R | Article 2 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1613
| 1614 | EnergyStatistics3 | U32 | 0.01 | kWh |  |  | R | Article 3 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1615
| 1616 | EnergyStatistics4 | U32 | 0.01 | kWh |  |  | R | Article 4 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1617
| 1618 | EnergyStatistics5 | U32 | 0.01 | kWh |  |  | R | Article 5 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1619
| 161A | EnergyStatistics6 | U32 | 0.01 | kWh |  |  | R | Article 6 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
161B
| 161C | EnergyStatistics7 | U32 | 0.01 | kWh |  |  | R | Article 7 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
161D
| 161E | EnergyStatistics8 | U32 | 0.01 | kWh |  |  | R | Article 8 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
161F
| 1620 | EnergyStatistics9 | U32 | 0.01 | kWh |  |  | R | Article 9 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1621
| 1622 | EnergyStatistics10 | U32 | 0.01 | kWh |  |  | R | Article 10 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1623
| 1624 | EnergyStatistics11 | U32 | 0.01 | kWh |  |  | R | Article 11 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1625
| 1626 | EnergyStatistics12 | U32 | 0.01 | kWh |  |  | R | Article 12 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1627
| 1628 | EnergyStatistics13 | U32 | 0.01 | kWh |  |  | R | Article 13 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1629
| 162A | EnergyStatistics14 | U32 | 0.01 | kWh |  |  | R | Article 14 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
162B
| 162C | EnergyStatistics15 | U32 | 0.01 | kWh |  |  | R | Article 15 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
162D
| 162E | EnergyStatistics16 | U32 | 0.01 | kWh |  |  | R | Article 16 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
162F
| 1630 | EnergyStatistics17 | U32 | 0.01 | kWh |  |  | R | Article 17 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1631
| 1632 | EnergyStatistics18 | U32 | 0.01 | kWh |  |  | R | Article 18 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1633
| 1634 | EnergyStatistics19 | U32 | 0.01 | kWh |  |  | R | Article 19 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1635
| 1636 | EnergyStatistics20 | U32 | 0.01 | kWh |  |  | R | Article 20 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1637
| 1638 | EnergyStatistics21 | U32 | 0.01 | kWh |  |  | R | 21. Historical Energy Statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1639
| 163A | EnergyStatistics22 | U32 | 0.01 | kWh |  |  | R | 22. Historical Energy Statistics. Refer to the energy statistics return setting register for the corresponding date and time.
163B
| 163C | EnergyStatistics23 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 23. Refer to the energy statistics return setting register for the corresponding date and time.
163D
| 163E | EnergyStatistics24 | U32 | 0.01 | kWh |  |  | R | 24. Historical Energy Statistics. Refer to the energy statistics return setting register for the corresponding date and time.
163F
| 1640 | EnergyStatistics25 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 25. Refer to the energy statistics return setting register for the corresponding date and time.
1641
| 1642 | EnergyStatistics26 | U32 | 0.01 | kWh |  |  | R | Article 26 of Historical Energy Statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1643
| 1644 | EnergyStatistics27 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 27. Refer to the energy statistics return setting register for the corresponding date and time.
1645
| 1646 | EnergyStatistics28 | U32 | 0.01 | kWh |  |  | R | 28. Historical Energy Statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1647
| 1648 | EnergyStatistics29 | U32 | 0.01 | kWh |  |  | R | Article 29 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1649
| 164A | EnergyStatistics30 | U32 | 0.01 | kWh |  |  | R | Article 30 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
164B
| 164C | EnergyStatistics31 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 31. Refer to the energy statistics return setting register for the corresponding date and time.
164D
| 164E | EnergyStatistics32 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 32. Refer to the energy statistics return setting register for the corresponding date and time.
164F
| 1650 | EnergyStatistics33 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 33. Refer to the energy statistics return setting register for the corresponding date and time.
1651
| 1652 | EnergyStatistics34 | U32 | 0.01 | kWh |  |  | R | Article 34 of Historical Energy Statistics. Refer to the energy statistics return setting register for the corresponding date and time.
1653
| 1654 | EnergyStatistics35 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 35. Refer to the energy statistics return setting register for the corresponding date and time.
1655
| 1656 | EnergyStatistics36 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 36. Refer to the energy statistics return setting register for the corresponding date and time.
1657
| 1658 | EnergyStatistics37 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 37. Refer to the energy statistics return setting register for the corresponding date and time.
1659
| 165A | EnergyStatistics38 | U32 | 0.01 | kWh |  |  | R | Article 38 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
165B
| 165C | EnergyStatistics39 | U32 | 0.01 | kWh |  |  | R | Article 39 of historical energy statistics. Refer to the energy statistics return setting register for the corresponding date and time.
165D
| 165E | EnergyStatistics40 | U32 | 0.01 | kWh |  |  | R | Historical Energy Statistics Article 40. Refer to the energy statistics return setting register for the corresponding date and time.
165F
Core function configuration (0x2000-0x207F)
| 2000 | AddressMask_Config_Core1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
2001
2002
2003
| 2004 | Country_Code | U16 |  |  |  |  | RW | Safety country for storage
| 2005 | Safety_Version | U16 |  |  |  |  | RW | The safety parameter version number of the communication host (host computer).
| 2006 | Factory_Reset | U16 |  |  | 1 | 255 | RW | Restore factory registers; the bit value is1 efficient.Bit0 : Clear the batteryBit1 : Clear the event logBit2 : When all function configuration parameters are restored to their default values, the state of the last write operation is returned:0x0000:success0x0001-0x00FF : in operation0xFFFB : Operation failed, controller refused to respond (maybe controller is busy or misconfigured)0xFFFC : Operation failed, no response from the controller0xFFFD : Operation failed, the current function is disabled0xFFFE : Operation failed, parameter access failed0xFFFF: Operation failed, input parameters are incorrect
| 2007 | Safety_Name1 | ASCII |  |  |  |  | RW | Safety country name No.1,2bit. register high8Place the name of the safety code1bit; register low8Place the name of the safety code2bit.
| 2008 | Safety_Name2 | ASCII |  |  |  |  | RW | Safety country name No.3,4bit. register high8Place the name of the safety code3bit; register low8Place the name of the safety code4bit.
| 2009 | Safety_Name3 | ASCII |  |  |  |  | RW | Safety country name No.5,6bit. register high8Place the name of the safety code5bit; register low8Place the name of the safety code6bit.
| 200A | Safety_Name4 | ASCII |  |  |  |  | RW | Safety country name No.7,8bit. register high8Place the name of the safety code7bit; register low8Place the name of the safety code8bit.
| 200B | Safety_Name5 | ASCII |  |  |  |  | RW | Safety country name No.9,10bit. register high8Place the name of the safety code9bit; register low8Place the name of the safety code10bit.
200C
| 200D | Commu_protocol_type | U16 |  |  |  |  | RW | Protocol setting register: 0x0000: modbus_RTU protocol; 0x0001: modbus_Korea protocol; 0x0002: sofar_sgp_normal standard protocol; 0x0003: sofar_sgp_advance advanced protocol; 0x0004: sunspec protocol; 0x0005: solarmax protocol;
200E
200F
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
201A
201B
201C
201D
201E
201F
2020
2021
2022
2023
2024
2025
2026
2027
2028
2029
202A
202B
202C
202D
202E
202F
2030
2031
2032
2033
2034
2035
2036
2037
2038
| 2039 | Upgrade_Total | U16 |  |  |  |  | R | The total number of upgrade targets. When one or more targets are upgraded simultaneously with the same firmware, the value of this register represents the total number of upgrade targets.
| 203A | Upgrade_Result_Table1 | U16 |  |  |  |  | R | Upgrade result bit table 1. A bit value of 0 indicates that the upgrade is not completed or failed; a bit value of 1 indicates that the upgrade is successful. The least significant bit represents the upgrade target numbered 1. The highest bit represents the upgrade target numbered 16.
| 203B | Upgrade_Result_Table2 | U16 |  |  |  |  | R | Upgrade result bit table 2. A bit value of 0 indicates that the upgrade is not completed or failed; a bit value of 1 indicates that the upgrade is successful. The lowest bit represents the upgrade target numbered 17. The highest bit represents the upgrade target numbered 32.
| 203C | Remote_Download_Control | U16 |  |  |  |  | W | Remote download control register. (Only single target operation is supported) High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded. The explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (sub DSP); Bit3: Fuse; Bit4: BMS; Bit5: PCU; Bit6: BDU;
| 203D | Remote_Upgrade_Control | U16 |  |  |  |  | W | Remote upgrade control register. (Only single target operation is supported) High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded. The explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (sub DSP); Bit3: Fuse; Bit4: BMS; Bit5: PCU; Bit6: BDU;
| 203E | Local_Upgrade_Control | U16 |  |  |  |  | W | high byte. write0xA5 efficient. The low byte contains the chip combination that needs to be upgraded, and each bit is explained as follows:Bit0 : communication board;Bit1: control panel1(hostDSP );Bit2: control panel2(viceDSP );Bit3:Fuse; Bit4: BMS; Bit5: PCU; Bit6: BDU;
| 203F | Local_Upgrade_Status | U16 |  |  |  |  | R | The high byte of the current upgrade progress indicates the current upgrade target chip:0x00 : not in upgrade state;0x01:hostDSP upgrade;0x02:viceDSP upgrade;0x03:ARM upgrade;0x04:FUSEupgrade; 0x05: BMS upgrade; 0x06: PCU upgrade; 0x07: BDU upgrade; the low byte indicates the current upgrade progress: Progress range0-100%;
Power carrier communicationPLCparameter area(0x2100-0x213F)
| 2100 | AddressMask_Plc_Info | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid. | installer
| 2101 | [8 empty] | installer
| 2102 | [8 empty] | installer
| 2103 | [8 empty] | installer
| 2104 | PLC_Type | U16 | 1 |  |  |  | R | CCOandSTAshared properties,PLCType: Hidden property, only need to show numbers
| 2105 | PLC_Soft_Ver1 | ASCII | 1 |  |  |  | R | CCOandSTAShared properties PLCsoftware version maximum30byte,ver1
| 2106 | PLC_Soft_Ver2 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver2
| 2107 | PLC_Soft_Ver3 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver3
| 2108 | PLC_Soft_Ver4 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver4
| 2109 | PLC_Soft_Ver5 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver5
| 210A | PLC_Soft_Ver6 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver6
| 210B | PLC_Soft_Ver7 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver7
| 210C | PLC_Soft_Ver8 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver8
| 210D | PLC_Soft_Ver9 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver9
| 210E | PLC_Soft_Ver10 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver10
| 210F | PLC_Soft_Ver11 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver11
| 2110 | PLC_Soft_Ver12 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver12
| 2111 | PLC_Soft_Ver13 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver13
| 2112 | PLC_Soft_Ver14 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver14
| 2113 | PLC_Soft_Ver15 | ASCII | 1 |  |  |  | R | PLCsoftware version maximum30byte,ver15
| 2114 | PLC_Sta_Net_State | U16 | 1 |  |  |  | R | STAUnique property PLC,STAread network status,1-Indicates that it is connected to the network,2-Indicates not connected to the network;CCOreturn on read0
| 2115 | PLC_Cco_Mac | U16 | 1 |  |  |  | R | STAUnique property STAafter the networkCCOAddress, if not connected to the network, fill in0,CCODevice access, fill in0 PLCofMACtotal address6bytes, high2byteregister high8bit storage1byte;register low8bit storage2byte.
| 2116 |  | U16 | 1 |  |  |  | R | PLCofMACtotal address6bytes, medium2byteregister high8bit storage3byte;register low8bit storage4byte.
| 2117 |  | U16 | 1 |  |  |  | R | PLCofMACtotal address6byte, low2byteregister high8bit storage5byte;register low8bit storage6byte.
| 2118 | PLC_Com_Property | U16 | 1 |  |  |  | RW | CCOandSTAShared properties bit0-bit1: 0~1correspond1/1.5 bit2~bit4:0~7correspondNONE/odd/EVENThree verification methods bit5~bit7 0~1correspond8/9Two data bit lengthsbit8~15 0~4correspond4800/9600/19200/38400/115200
| 2119 | PLC_Mac_Addr | U16 | 1 |  |  |  | RW | CCOandSTAShared properties PLCofMACtotal address6bytes, high2byteregister high8bit storage1byte;register low8bit storage2byte.
| 211A |  | U16 | 1 |  |  |  | RW | PLCofMACtotal address6bytes, medium2byteregister high8bit storage3byte;register low8bit storage4byte.
| 211B |  | U16 | 1 |  |  |  | RW | PLCofMACtotal address6byte, low2byteregister high8bit storage5byte;register low8bit storage6byte.
| 211C | PLC_BandChnl | U16 | 1 |  |  |  | R(W) | CCO and STA share attributes, STA is read-only, CCO can read and write 5 values of frequency band information, enumeration: 1/4/5/7/8
| 211D | PLC_TxPower | U16 | 1 |  |  |  | RW | CCO and STA share the attribute high transmit power8Bits represent analog power, range: 0-10Low8Bit represents digital power, range: 0-55 (subtract 40 in actual use)
| 211E | PLC_Whitelist_ExeType | U16 | 1 |  |  |  | RW | CCO unique attribute whitelist operation type, write-only register, return 0 when read 1-delete all whitelists; 2-delete list whitelist; 3-write list whitelist; 4-read whitelist The starting number and number of the whitelist for the next read)
| 211F | PLC_WhitelistCount | U16 | 1 |  |  |  | RW | The total number of CCO unique attribute whitelists, up to 30
| 2120 | PLC_Whitelist_StartAndCount | U16 | 1 |  |  |  | RW | CCO unique attribute whitelist operation start number and quantity The high 8 bits represent the start number, the range is 1-30 The lower 8 bits represent the number of operations, the range is 1-5
| 2121 | PLC_Whitelist0 | U16 | 1 |  |  |  | RW | CCO unique attribute whitelist 0, high 2 bytes
| 2122 |  | U16 | 1 |  |  |  | RW | Whitelist 0, medium 2 bytes
| 2123 |  | U16 | 1 |  |  |  | RW | Whitelist 0, lower 2 bytes
| 2124 | PLC_Whitelist1 | U16 | 1 |  |  |  | RW | Whitelist 1, high 2 bytes
| 2125 |  | U16 | 1 |  |  |  | RW | Whitelist 1, medium 2 bytes
| 2126 |  | U16 | 1 |  |  |  | RW | Whitelist 1, lower 2 bytes
| 2127 | PLC_Whitelist2 | U16 | 1 |  |  |  | RW | Whitelist 2, high 2 bytes
| 2128 |  | U16 | 1 |  |  |  | RW | Whitelist 2, medium 2 bytes
| 2129 |  | U16 | 1 |  |  |  | RW | Whitelist 2, lower 2 bytes
| 212A | PLC_Whitelist3 | U16 | 1 |  |  |  | RW | Whitelist 3, high 2 bytes
| 212B |  | U16 | 1 |  |  |  | RW | Whitelist 3, medium 2 bytes
| 212C |  | U16 | 1 |  |  |  | RW | Whitelist 3, lower 2 bytes
| 212D | PLC_Whitelist4 | U16 | 1 |  |  |  | RW | Whitelist 4, high 2 bytes
| 212E |  | U16 | 1 |  |  |  | RW | Whitelist 4, medium 2 bytes
| 212F |  | U16 | 1 |  |  |  | RW | Whitelist 4, lower 2 bytes
| 2130 | PLC_Reset | U16 | 1 |  |  |  | W | CCO unique attribute, can only be written, 1-means module reset read meaningless return data 0
2131
2132
2133
2134
2135
2136
2137
2138
2139
213A
213B
213C
213D
213E
213F
PCU&BDUdata area(0x6000-0x6FFF)
| 6000 | AddressMask_PCU1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
6001
6002
6003
| 6004 | PCU_Number | [5 empty] | R | Total number of PCU online.
| 6005 | [6 empty] | R | Summary information reservation
| 6006 | [6 empty] | R | Summary information reservation
| 6007 | [6 empty] | R | Summary information reservation
| 6008 | [6 empty] | R | Summary information reservation
| 6009 | [6 empty] | R | Summary information reservation
| 600A | [6 empty] | R | Summary information reservation
| 600B | [6 empty] | R | Summary information reservation
| 600C | [6 empty] | R | Summary information reservation
| 600D | [6 empty] | R | Summary information reservation
| 600E | [6 empty] | R | Summary information reservation
| 600F | [6 empty] | R | Summary information reservation
| 6010 | PCU_ID | U16 |  |  |  |  | R | PCU number. Numbering starts at 1.
| 6011 | PCU_SN0 | ASCII |  |  |  |  | R | PCU serial number 0
| 6012 | PCU_SN1 | ASCII |  |  |  |  | R | PCU serial number 1
| 6013 | PCU_SN2 | ASCII |  |  |  |  | R | PCU serial number 2
| 6014 | PCU_SN3 | ASCII |  |  |  |  | R | PCU serial number 3
| 6015 | PCU_SN4 | ASCII |  |  |  |  | R | PCU serial number 4
| 6016 | PCU_SN5 | ASCII |  |  |  |  | R | PCU serial number 5
| 6017 | PCU_SN6 | ASCII |  |  |  |  | R | PCU serial number 6
| 6018 | PCU_SN7 | ASCII |  |  |  |  | R | PCU serial number 7
| 6019 | PCU_SN8 | ASCII |  |  |  |  | R | PCU serial number 8
| 601A | PCU_SN9 | ASCII |  |  |  |  | R | PCU serial number 9
| 601B | PCU_Software_Version1 | ASCII |  |  |  |  | R | software version number1
| 601C | PCU_Software_Version2 | ASCII |  |  |  |  | R | software version number2
| 601D | PCU_Hardware_Version | U16 |  |  |  |  | R | Hardware version number
| 601E | PCU_Can1_Version | U16 |  |  |  |  | R | CAN1Protocol version number
| 601F | PCU_Can2_Version | U16 |  |  |  |  | R | CAN2Protocol version number
| 6020 | PCU_Work_State | U16 |  |  |  |  | R | Module Status 0: Wait Upgrade 1: Check 2: Normal 3: Battery Active 4: Fault 5: Permanent Fault
| 6021 | PCU_Internal_Temperature | U16 | 1 | °C |  |  | R | Chassis internal temperature
| 6022 | PCU_Radiator_Temperature1 | I16 | 1 | °C |  |  | R | heat sink1temperature
| 6023 | PCU_Radiator_Temperature2 | I16 | 1 | °C |  |  | R | heat sink2temperature
| 6024 | PCU_Warning1 | U16 |  |  |  |  | R | warn1
| 6025 | PCU_Warning2 | U16 |  |  |  |  | R | warn2
| 6026 | PCU_Warning3 | U16 |  |  |  |  | R | warn3
| 6027 | PCU_Warning4 | U16 |  |  |  |  | R | warn4
| 6028 | PCU_Fault1 | U16 |  |  |  |  | R | Fault1
| 6029 | PCU_Fault2 | U16 |  |  |  |  | R | Fault2
| 602A | PCU_Fault3 | U16 |  |  |  |  | R | Fault3
| 602B | PCU_Fault4 | U16 |  |  |  |  | R | Fault4
| 602C | PCU_DC_High_Voltage | U16 | 0.1 | V | 0 |  | R | DCHigh side voltage
| 602D | PCU_DC_Low_Voltage | U16 | 0.1 | V | 0 |  | R | DCLow side voltage
| 602E | PCU_Low_Current | I16 | 0.1 | A |  |  | R | DCLow side current
| 602F | PCU_Low_Power | I16 | 0.01 | kW |  |  | R | DCLow side power
| 6030 | PCU_BusP | U16 | 0.1 | V |  |  | R | Positive bus voltage
| 6031 | PCU_BusN | U16 | 0.1 | V |  |  | R | Negative bus voltage
| 6032 | PCU_FC_Voltage1 | U16 | 0.1 | V |  |  | R | Flying capacitor voltage 1
| 6033 | PCU_FC_Voltage2 | U16 | 0.1 | V |  |  | R | Flying capacitor voltage 2
| 6034 | PCU_FC_Voltage3 | U16 | 0.1 | V |  |  | R | Flying capacitor voltage 3
| 6035 | PCU_FC_Voltage4 | U16 | 0.1 | V |  |  | R | Flying capacitor voltage 4
| 6036 | PCU_IL_Current1 | I16 | 0.1 | A |  |  | R | Inductor current branch 1
| 6037 | PCU_IL_Current2 | I16 | 0.1 | A |  |  | R | Inductor current branch 2
| 6038 | PCU_IL_Current3 | I16 | 0.1 | A |  |  | R | Inductor current branch 3
| 6039 | PCU_IL_Current4 | I16 | 0.1 | A |  |  | R | Inductor current branch 4
| 603A | [6 empty] | R
| 603B | [6 empty] | R
| 603C | [6 empty] | R
| 603D | [6 empty] | R
| 603E | [6 empty] | R
| 603F | [6 empty] | R
| 6040 | AddressMask_PCU2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
6041
6042
6043
| 6044 | PCU_Inquire | U16 |  |  | 1 | 32 | RW | PCUQuery the control word.By setting this register to select the need to read or setPCUmodule.
| 6045 | PCU_Remote_On_Off | U16 |  |  | 0 | 3 | RW | DC module remote switch 0: shutdown 1: prohibit charging 2: prohibit discharging 3: allow charging and discharging
| 6046 | PCU_Max_Charge_Current | U16 | 0.1 | A | 0 | 65535 | RW | DC module maximum charging current
| 6047 | PCU_Max_Discharge_Current | U16 | 0.1 | A | 0 | 65535 | RW | DC module maximum discharge current
| 6048 | K_Voltage_HVbus | U16 | 0.001 | pu | 950 | 1050 | RW | High side hvbus voltage calibration ratio
| 6049 | K_Voltage_Pbus | U16 | 0.001 | pu | 950 | 1050 | RW | High side pbus voltage calibration ratio
| 604A | K_Current_HV_Chg | U16 | 0.001 | pu | 950 | 1050 | RW | High Side Charge Current Calibration Ratio
| 604B | K_Current_HV_Dchg | U16 | 0.001 | pu | 950 | 1050 | RW | High Side Discharge Current Calibration Ratio
| 604C | K_Voltage_LV | U16 | 0.001 | pu | 950 | 1050 | RW | Low Side Voltage Calibration Ratio
| 604D | K_Current_LV_Chg | U16 | 0.001 | pu | 950 | 1050 | RW | Low-Side Charge Current Calibration Ratio
| 604E | K_Current_LV_Dchg | U16 | 0.001 | pu | 950 | 1050 | RW | Low Side Discharge Current Calibration Ratio
604F
6050
6051
6052
6053
6054
6055
6056
6057
6058
6059
605A
605B
605C
605D
605E
605F
6060
6061
6062
6063
6064
6065
6066
6067
6068
6069
606A
606B
606C
606D
606E
606F
6070
6071
6072
6073
6074
6075
6076
6077
6078
6079
607A
607B
607C
607D
607E
607F
| 6080 | AddressMask_BDU1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
6081
6082
6083
| 6084 | BDU_Number | U16 |  |  |  |  | R | Total number of BDUs online.
| 6085 | [6 empty] | R | Summary information reservation
| 6086 | [6 empty] | R | Summary information reservation
| 6087 | [6 empty] | R | Summary information reservation
| 6088 | [6 empty] | R | Summary information reservation
| 6089 | [6 empty] | R | Summary information reservation
| 608A | [6 empty] | R | Summary information reservation
| 608B | [6 empty] | R | Summary information reservation
| 608C | [6 empty] | R | Summary information reservation
| 608D | [6 empty] | R | Summary information reservation
| 608E | [6 empty] | R | Summary information reservation
| 608F | [6 empty] | R | Summary information reservation
| 6090 | BDU_ID | U16 |  |  |  |  | R | BDU number. Numbering starts at 1.
| 6091 | BDU_SN0 | ASCII |  |  |  |  | R | BDU serial number 0
| 6092 | BDU_SN1 | ASCII |  |  |  |  | R | BDU serial number 1
| 6093 | BDU_SN2 | ASCII |  |  |  |  | R | BDU serial number 2
| 6094 | BDU_SN3 | ASCII |  |  |  |  | R | BDU serial number 3
| 6095 | BDU_SN4 | ASCII |  |  |  |  | R | BDU serial number 4
| 6096 | BDU_SN5 | ASCII |  |  |  |  | R | BDU serial number 5
| 6097 | BDU_SN6 | ASCII |  |  |  |  | R | BDU serial number 6
| 6098 | BDU_SN7 | ASCII |  |  |  |  | R | BDU serial number 7
| 6099 | BDU_SN8 | ASCII |  |  |  |  | R | BDU serial number 8
| 609A | BDU_SN9 | ASCII |  |  |  |  | R | BDU serial number 9
| 609B | Software_Version_Stage_BDU | ASCII |  |  |  |  | R | BDU chip software version number stage definition bit. register low8bit storageASCIIcode. The default for the official version is'V'.
| 609C | Software_Version_Major_BDU | ASCII |  |  |  |  | R | The main version number of the BDU chip software. The main version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number.
| 609D | Software_Version_Custom_BDU | ASCII |  |  |  |  | R | BDU chip software non-standard customized version number. The version number of the positive standard software is"00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. register high8The bit stores the high-order number; the register is low8The bits store the low-order digits.
| 609E | Software_Version_Minor_BDU | ASCII |  |  |  |  | R | BDU chip software subversion number. The high-order 8 bits of the register store the high-order number; the low-order 8 bits of the register store the low-order number.
| 609F | BDU_Fault1 | U16 |  |  |  |  | R | BDUaccident details1
| 60A0 | BDU_Battery_Number | U16 |  |  |  |  | R | Number of cells in a single cluster
| 60A1 | TotalNum_PV | U16 | 1 |  |  |  | R | The total number of strings
| 60A2 | TotalNum_Battery | U16 | 1 |  |  |  | R | Total number of batteries
60A3
60A4
60A5
60A6
60A7
60A8
60A9
60AA
60AB
60AC
60AD
60AE
60AF
60B0
60B1
60B2
60B3
60B4
60B5
60B6
60B7
60B8
60B9
60BA
60BB
60BC
60BD
60BE
60BF
| 60C0 | AddressMask_BDU2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
60C1
60C2
60C3
| 60C4 | BDU_Inquire | U16 |  |  | 1 |  | RW | BDUQuery the control word.By setting this register to select the need to read or setBDUmodule.
| 60C5 | RatedPower_N_ID | U16 | 1 |  | 255 |  | RW | Operate the number of the specified number of channels, the value is within the total number of channels in the string, starting from 1
| 60C6 | RatedPower_N_PV | U16 | 1 |  |  |  | R | String rated power of the specified number of channels
| 60C7 | RatedPower_N_Battery | U16 | 1 |  |  |  | R | The rated power of the battery for the specified number of channels
ODM data customization area (0x7000-0x707F)
| 7000 |  | ASCII |  |  |  |  | RW | The address of 0x7000-0x707F is a custom area, which must meet the following formats: All registers in this area are in ASCII format, the upper 8 bits of the register store the front-end characters, and the lower 8 bits store the back-end characters. For example, when the string "1234" is stored in 0x7000 and 0x7001, the data in 0x7000 is 0x3132; the data in 0x7001 is 0x3334. Allowed characters include: 0x20-0x7E and 0xFF. 0xFF is automatically ignored when parsing. The string format is defined as follows: key1=value1\r\nkey2=value2\r\n The keys supported by this protocol version are: "SN": ODM serial number "machine": ODM model | end user
BMSTransparent transmission area (0x9000-0x9FFF)
| 9000 | AddressMask_BMS1_System | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
9001
9002
9003
| 9004 | BMS_Sys_Time | U32 |  |  |  |  | R | BMS system clock Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting in 2000)
9005
| 9006 | BMS_CAN_Version | U16 |  |  |  |  | R | CANProtocol version number
| 9007 | BMS_Manufacture_Name0 | U16 |  |  |  |  | R | Manufacturer information0
| 9008 | BMS_Manufacture_Name1 | U16 |  |  |  |  | R | Manufacturer information1
| 9009 | BMS_Manufacture_Name2 | U16 |  |  |  |  | R | Manufacturer information2
| 900A | BMS_Manufacture_Name3 | U16 |  |  |  |  | R | Manufacturer information3
| 900B | BMS_Version | U16 |  |  |  |  | R | BMSversion number
| 900C | Cell_Type | U16 |  |  |  |  | R | Cell type
| 900D | BaPack_Number | U16 |  |  |  |  | R | high8Bit: Low number of parallel battery packs8Bit: Number of strings in all battery packs
| 900E | Realtime_Capacity | U16 | 1 | % |  |  | R | real-time remaining capacity
| 900F | Total_Voltage | U16 | 0.1 | V |  |  | R | total voltage
| 9010 | Total_Current | I16 | 0.1 | A |  |  | R | total current
| 9011 | Cell_Average_Temperature | U16 | 0.1 | °C |  |  | R | Average cell temperature
| 9012 | SOC | U16 | 1 | % |  |  | R | state of charge
| 9013 | SOH | U16 | 1 | % |  |  | R | health
| 9014 | BMS_Sys_Protect0 | U16 |  |  |  |  | R | BMSSystem Protection Information0
| 9015 | BMS_Sys_Protect1 | U16 |  |  |  |  | R | BMSSystem Protection Information1
| 9016 | BMS_Sys_Alarm0 | U16 |  |  |  |  | R | BMSSystem alarm information0
| 9017 | BMS_Sys_Alarm1 | U16 |  |  |  |  | R | BMSSystem alarm information1
9018
9019
901A
901B
901C
901D
901E
901F
| 9020 | BMS_Inquire | U16 |  |  |  |  | RW | Battery query control word Bit0-7: The query battery pack serial number, the valid range is 0~15, 0 means the first battery pack Bit8-11: The query battery pack serial number, the valid range is 0~15, 0 means the first battery pack Bit12- 15: The fault serial number to be queried, the valid range is 0~5, 0 means the most recent fault
9021
9022
9023
9024
9025
9026
9027
9028
9029
902A
902B
902C
902D
902E
902F
9030
9031
9032
9033
9034
9035
9036
9037
9038
9039
903A
903B
903C
903D
903E
903F
| 9040 | AddressMask_BMS2_Realtime | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
9041
9042
9043
| 9044 | Pack_RT_ID | U16 |  |  |  |  | R | Real-time data battery pack number. high8Bit: battery pack serial number low8Bit: battery pack serial number
| 9045 | Pack_RT_Timestamp | U32 |  |  |  |  | R | real-time data timestamp
9046
| 9047 | Pack_RT_SN0 | U16 |  |  |  |  | R | devise serial number0
| 9048 | Pack_RT_SN1 | U16 |  |  |  |  | R | devise serial number1
| 9049 | Pack_RT_SN2 | U16 |  |  |  |  | R | devise serial number2
| 904A | Pack_RT_SN3 | U16 |  |  |  |  | R | devise serial number3
| 904B | Pack_RT_SN4 | U16 |  |  |  |  | R | devise serial number4
| 904C | Pack_RT_SN5 | U16 |  |  |  |  | R | devise serial number5
| 904D | Pack_RT_SN6 | U16 |  |  |  |  | R | devise serial number6
| 904E | Pack_RT_SN7 | U16 |  |  |  |  | R | devise serial number7
| 904F | Pack_RT_SN8 | U16 |  |  |  |  | R | devise serial number8
| 9050 | Pack_RT_SN9 | U16 |  |  |  |  | R | devise serial number9
| 9051 | Pack_RT_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage
| 9052 | Pack_RT_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage
| 9053 | Pack_RT_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage
| 9054 | Pack_RT_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage
| 9055 | Pack_RT_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage
| 9056 | Pack_RT_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage
| 9057 | Pack_RT_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage
| 9058 | Pack_RT_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage
| 9059 | Pack_RT_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage
| 905A | Pack_RT_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 Voltage
| 905B | Pack_RT_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 Voltage
| 905C | Pack_RT_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 Voltage
| 905D | Pack_RT_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 Voltage
| 905E | Pack_RT_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 Voltage
| 905F | Pack_RT_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 Voltage
| 9060 | Pack_RT_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 Voltage
| 9061 | Pack_RT_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 Voltage
| 9062 | Pack_RT_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage
| 9063 | Pack_RT_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 Voltage
| 9064 | Pack_RT_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage
| 9065 | Pack_RT_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 Voltage
| 9066 | Pack_RT_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Cell 22 Voltage
| 9067 | Pack_RT_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Cell 23 voltage
| 9068 | Pack_RT_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage
| 9069 | Pack_RT_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | Cell maximum voltage
| 906A | Pack_RT_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum cell voltage
| 906B | Pack_RT_Temperature1_Pack | I16 | 0.1 | °C |  |  | R | battery pack temperature 1
| 906C | Pack_RT_Temperature2_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 2
| 906D | Pack_RT_Temperature3_Pack | I16 | 0.1 | °C |  |  | R | battery pack temperature 3
| 906E | Pack_RT_Temperature4_Pack | I16 | 0.1 | °C |  |  | R | battery pack temperature4
| 906F | Pack_RT_Temperature_MOS | I16 | 0.1 | °C |  |  | R | MOSTube temperature
| 9070 | Pack_RT_Temperature_Env | I16 | 0.1 | °C |  |  | R | Ambient temperature inside the battery pack
| 9071 | Pack_RT_Current | I16 | 0.1 | A |  |  | R | battery pack current
| 9072 | Pack_RT_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity
| 9073 | Pack_RT_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | full capacity
| 9074 | Pack_RT_Cycles | U16 | 1 | times |  |  | R | Cycles
| 9075 | Pack_RT_Balance_State | U16 |  |  |  |  | R | Equilibrium
| 9076 | Pack_RT_Alarm_State | U16 |  |  |  |  | R | Alarm status
| 9077 | Pack_RT_Protect_State | U16 |  |  |  |  | R | Protection status
| 9078 | Pack_RT_Fault_State | U16 |  |  |  |  | R | fault state
| 9079 | Pack_RT_Total_Voltage | U16 | 0.1 | V |  |  | R | total voltage
| 907A | Pack_RT_SOC | U16 | 1 | % |  |  | R | SOC
| 907B | Pack_RT_Pack_Number | U16 |  |  |  |  | R | The total number of battery packs in this group of batteries
| 907C | Pack_RT_Cell_Number | U16 |  |  |  |  | R | The number of battery cell strings in a single battery pack of this group
907D
907E
907F
| 9080 | AddressMask_BMS3_Fault | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above (including the address of this field) of this field. bit4 represents the address where the highest-order address of this field plus 1 is located. 0 means invalid; 1 means valid.
9081
9082
9083
| 9084 | Pack_Fault_ID | U16 |  |  |  |  | R | Real-time fault battery pack number. Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, 0 means the first battery pack Bit12-15: The query Fault serial number, the valid range is 0~5, 0 means the most recent fault
| 9085 | Pack_Fault_Timestamp | U32 |  |  |  |  | R | Failure data timestamp
9086
| 9087 | Pack_Fault_SN0 | U16 |  |  |  |  | R | devise serial number0
| 9088 | Pack_Fault_SN1 | U16 |  |  |  |  | R | devise serial number1
| 9089 | Pack_Fault_SN2 | U16 |  |  |  |  | R | devise serial number2
| 908A | Pack_Fault_SN3 | U16 |  |  |  |  | R | devise serial number3
| 908B | Pack_Fault_SN4 | U16 |  |  |  |  | R | devise serial number4
| 908C | Pack_Fault_SN5 | U16 |  |  |  |  | R | devise serial number5
| 908D | Pack_Fault_SN6 | U16 |  |  |  |  | R | devise serial number6
| 908E | Pack_Fault_SN7 | U16 |  |  |  |  | R | devise serial number7
| 908F | Pack_Fault_SN8 | U16 |  |  |  |  | R | devise serial number8
| 9090 | Pack_Fault_SN9 | U16 |  |  |  |  | R | devise serial number9
| 9091 | Pack_Fault_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage
| 9092 | Pack_Fault_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage
| 9093 | Pack_Fault_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage
| 9094 | Pack_Fault_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage
| 9095 | Pack_Fault_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage
| 9096 | Pack_Fault_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage
| 9097 | Pack_Fault_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage
| 9098 | Pack_Fault_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage
| 9099 | Pack_Fault_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage
| 909A | Pack_Fault_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 Voltage
| 909B | Pack_Fault_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 Voltage
| 909C | Pack_Fault_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 Voltage
| 909D | Pack_Fault_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 Voltage
| 909E | Pack_Fault_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 Voltage
| 909F | Pack_Fault_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 Voltage
| 90A0 | Pack_Fault_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 Voltage
| 90A1 | Pack_Fault_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 Voltage
| 90A2 | Pack_Fault_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage
| 90A3 | Pack_Fault_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 Voltage
| 90A4 | Pack_Fault_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage
| 90A5 | Pack_Fault_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 Voltage
| 90A6 | Pack_Fault_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Cell 22 Voltage
| 90A7 | Pack_Fault_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Cell 23 voltage
| 90A8 | Pack_Fault_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage
| 90A9 | Pack_Fault_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | Cell maximum voltage
| 90AA | Pack_Fault_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum cell voltage
| 90AB | Pack_Fault_Temperature1_Pack | I16 | 0.1 | °C |  |  | R | battery pack temperature 1
| 90AC | Pack_Fault_Temperature2_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 2
| 90AD | Pack_Fault_Temperature3_Pack | I16 | 0.1 | °C |  |  | R | battery pack temperature 3
| 90AE | Pack_Fault_Temperature4_Pack | I16 | 0.1 | °C |  |  | R | battery pack temperature4
| 90AF | Pack_Fault_Temperature_MOS | I16 | 0.1 | °C |  |  | R | MOSTube temperature
| 90B0 | Pack_Fault_Temperature_Env | I16 | 0.1 | °C |  |  | R | Ambient temperature inside the battery pack
| 90B1 | Pack_Fault_Current | I16 | 0.1 | A |  |  | R | battery pack current
| 90B2 | Pack_Fault_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity
| 90B3 | Pack_Fault_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | full capacity
| 90B4 | Pack_Fault_Total_Voltage | U16 | 0.01 | V |  |  | R | total voltage
| 90B5 | Pack_Alarm_State | U16 |  |  |  |  | R | Alarm status
| 90B6 | Pack_Protect_State | U16 |  |  |  |  | R | Protection status
| 90B7 | Pack_Fault_State | U16 |  |  |  |  | R | fault state
| 90B8 | Pack_Fault_Pack_Number | U16 |  |  |  |  | R | The total number of battery packs in this group of batteries
| 90B9 | Pack_Fault_Cell_Number | U16 |  |  |  |  | R | The number of battery cell strings in a single battery pack of this group
90BA
90BB
90BC
90BD
90BE
90BF
Note on G1145: PF1VK175: -10000~-8000 corresponds to power factor -1~-0.8
Note on H1145: PF1VK175: 8000~10000 corresponds to power factor 0.8~1

## Fault Bit Field Description
Table | Byte | Bit | bit field | Numbering | Remark | Alarm source | Classification | design classification
Fault1 | byte 0 | bit 0 | GridOVP | 001 | grid overvoltage | DSP | external | grid
|  | bit 1 | GridUVP | 002 | Grid undervoltage | DSP | external
|  | bit 2 | GridOFP | 003 | grid overfrequency | DSP | external
|  | bit 3 | GridUFP | 004 | Grid underfrequency | DSP | external
|  | bit 4 | GFCI | 005 | Leakage current fault | DSP | external
|  | bit 5 | OVRT | 006 | High wear error | DSP | external
|  | bit 6 | LVRT | 007 | low wear error | DSP | external
|  | bit 7 | IslandFault | 008 | island bug | DSP | external
| byte 1 | bit 0 | GridOVPInstant1 | 009 | Grid instantaneous value overvoltage 1 | DSP
|  | bit 1 | GridOVPInstant2 | 010 | Grid instantaneous value overvoltage 2 | DSP
|  | bit 2 | VGridLineFault | 011 | Grid line voltage error | DSP | external
|  | bit 3 | InvVoltFault | 012 | Inverter voltage error | DSP
|  | bit 4 | RefluxFault | 013 | Anti-reverse overload | DSP | external
|  | bit 5 | VGridUnbalance | 014 | grid voltage imbalance | DSP | external
|  | bit 6 | VGridNPEOver | 015 | Neutral ground voltage is too high
|  | bit 7 |  | 016
Fault2 | byte 0 | bit 0 | HwADErrIGrid | 017 | Grid current sampling error | DSP |  | sampling error
|  | bit 1 | HwADErrDCI(AC) | 018 | DCI sampling error (AC) | DSP
|  | bit 2 | HwADErrVGrid(DC) | 019 | Network voltage sampling error (DC) | DSP
|  | bit 3 | HwADErrVGrid(AC) | 020 | Network voltage sampling error (AC) | DSP
|  | bit 4 | HwGFCIFault(DC) | 021 | GFCI sampling error (DC) | DSP
|  | bit 5 | HwGFCIFault(AC) | 022 | GFCI sampling error (AC) | DSP
|  | bit 6 | HwADErrDCV | 023 | DCV sampling error | DSP
|  | bit 7 | HwADErrIdc | 024 | Input current sampling error | DSP
| byte 1 | bit 0 | HwADErrDCI(DC) | 025 | DCI sampling error (DC) | DSP
|  | bit 1 | HwADErrIdcBranch | 026 | Branch current sampling error | DSP
|  | bit 2 |  | 027
|  | bit 3 | PIDAbnormalOut | 028 | PID abnormal output
|  | bit 4 | ConsistentGFCI | 029 | Leakage current consistency error | DSP
|  | bit 5 | ConsistentVgrid | 030 | Network pressure consistency error | DSP
|  | bit 6 | ConsistentDCI | 031 | DCI Consistency Error | DSP
|  | bit 7 | N-PE fault | 032 | Neutral ground fault
Fault3 | byte 0 | bit 0 | SpiCommFault (DC) | 033 | SPI communication error (DC) | DSP
|  | bit 1 | SpiCommFault(AC) | 034 | SPI Communication Error (AC) | DSP
|  | bit 2 | SChip_Fault | 035 | Chip Error (DC) | DSP
|  | bit 3 | MChip_Fault | 036 | Chip Error (AC) | DSP
|  | bit 4 | HwAuxPowerFault | 037 | Auxiliary power error | DSP
|  | bit 5 | InvSoftStartFail | 038 | Inverter soft start failed | DSP
|  | bit 6 | ArcShutdownAlarm | 039 | Arc shutdown protection | DSP | external
|  | bit 7 | LowLightChkFail | 040 | Low light detection failed | DSP
| byte 1 | bit 0 | RelayFail | 041 | Relay detection failed | DSP |  | system
|  | bit 1 | IsoFault | 042 | Low insulation resistance | DSP | external
|  | bit 2 | PEConnectFault | 043 | ground fault | DSP | external
|  | bit 3 | InputConfigError | 044 | Input mode setting error | DSP | external
|  | bit 4 | CTDisconnect | 045 | CT error | DSP | external
|  | bit 5 | ReversalConnect | 046 | Input reverse connection error | DSP | external
|  | bit 6 | ParallelFault | 047 | Parallel error | DSP | external
|  | bit 7 | SNTypeFault | 048 | wrong serial number | DSP
Fault4 | byte 0 | bit 0 | TempErrBat | 049 | battery temperature protection | DSP | external | temperature
|  | bit 1 | TempErrHeatSink1 | 050 | Heatsink 1 temperature protection | DSP | external
|  | bit 2 | TempErrHeatSink2 | 051 | Heatsink 2 temperature protection | DSP | external
|  | bit 3 | TempErrHeatSink3 | 052 | Heatsink 3 temperature protection | DSP | external
|  | bit 4 | TempErrHeatSink4 | 053 | Heatsink 4 temperature protection | DSP | external
|  | bit 5 | TempErrHeatSink5 | 054 | Heatsink 5 temperature protection | DSP | external
|  | bit 6 | TempErrHeatSink6 | 055 | Radiator 6 temperature protection | DSP | external
|  | bit 7 |  | 056
| byte 1 | bit 0 | TempErrEnv1 | 057 | Ambient temperature 1 protection | DSP | external
|  | bit 1 | TempErrEnv2 | 058 | Ambient temperature 2 protection | DSP | external
|  | bit 2 | TempErrInv1 | 059 | Module 1 temperature protection | DSP | external
|  | bit 3 | TempErrInv2 | 060 | Module 2 temperature protection | DSP | external
|  | bit 4 | TempErrInv3 | 061 | Module 3 temperature protection | DSP | external
|  | bit 5 | TempDiffErrInv | 062 | Module temperature difference is too large | DSP
|  | bit 6 |  | 063
|  | bit 7 |  | 064
Fault5 | byte 0 | bit 0 | BusRmsUnbalance | 065 | Unbalanced bus rms | DSP |  | Overvoltage
|  | bit 1 | BusInstUnbalance | 066 | The instantaneous value of the bus is unbalanced | DSP
|  | bit 2 | BusUVP | 067 | Bus undervoltage during grid connection | DSP
|  | bit 3 | BusZVP | 068 | Bus low voltage | DSP
|  | bit 4 | PVOVP | 069 | PV overvoltage | DSP
|  | bit 5 | BatOVP | 070 | battery overvoltage | DSP
|  | bit 6 | LLCBusOVP | 071 | LLCBus Overvoltage Protection | DSP
|  | bit 7 | SwBusRmsOVP | 072 | Bus Rms software overvoltage | DSP
| byte 1 | bit 0 | SwBusIOVP | 073 | Instantaneous software overvoltage of bus | DSP
|  | bit 1 | FlyingCapOVP | 074 | Flying capacitor overvoltage protection | DSP
|  | bit 2 | FlyingCapUVP | 075 | Flying capacitor undervoltage protection | DSP
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
Fault6 | byte 0 | bit 0 | SwBatOCP | 081 | Battery overcurrent software protection | DSP |  | current
|  | bit 1 | DciOCP | 082 | Dci overcurrent protection | DSP
|  | bit 2 | SwIOCP | 083 | Output instantaneous current protection | DSP
|  | bit 3 | SwBuckBoostOCP | 084 | BckBst software overcurrent | DSP
|  | bit 4 | SwAcRmsOCP | 085 | Inverter Rms current protection | DSP
|  | bit 5 | SwPvOCPINstant | 086 | PV momentary software overcurrent | DSP
|  | bit 6 | IpvUnbalance | 087 | PV parallel unbalanced current | DSP
|  | bit 7 | IacUnbalance | 088 | Output current imbalance | DSP
| byte 1 | bit 0 | SwPvOCP | 089 | PV software overcurrent protection | DSP
|  | bit 1 | IbalanceOCP | 090 | Balanced circuit overcurrent protection | DSP
|  | bit 2 | ResOver | 091 | Resonance protection | DSP
|  | bit 3 | SwAcCBCFault | 092 | Software wave-by-wave current limiting protection | DSP
|  | bit 4 | SwPvBranchOCP | 093 | PVBranch software overcurrent
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
Fault7 | byte 0 | bit 0 | HwLLCBusOVP | 097 | LLC busbar hardware overvoltage | DSP |  | hardware signal
|  | bit 1 | HwBusOVP | 098 | Inverter bus hardware overvoltage | DSP
|  | bit 2 | HwBuckBoostOCP | 099 | BckBst hardware overcurrent | DSP
|  | bit 3 | HwBatOCP | 100 | Battery hardware overcurrent | DSP
|  | bit 4 |  | 101
|  | bit 5 | HwPVOCP | 102 | PV hardware overcurrent | DSP
|  | bit 6 | HwACOCP | 103 | AC output hardware overcurrent | DSP
|  | bit 7 |  | 104
| byte 1 | bit 0 | MeterCommFault | 105 | Electricity metercommunicationmistake | DSP | external | Hardware signal reservation, overload
|  | bit 1 | SNMachineFault | 106 | wrong serial number | DSP
|  | bit 2 | HwVerError | 107 | Hardware version mismatch
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 | Overload1 | 110 | Overload Protection 1 | DSP | external
|  | bit 6 | Overload2 | 111 | Overload Protection 2 | DSP | external
|  | bit 7 | Overload3 | 112 | Overload Protection 3 | DSP | external
Fault8 | byte 0 | bit 0 | OverTempDerating | 113 | Over temperature derating | DSP | external, prompt | load down | The fault word is only used to generate an alarm, notdirectMakes the system into a fault state.
|  | bit 1 | FreqDerating | 114 | frequency derating | DSP | external, prompt
|  | bit 2 | FreqLoading | 115 | frequency loading | DSP | external, prompt
|  | bit 3 | VoltDerating | 116 | voltage drop | DSP | external, prompt
|  | bit 4 | VoltLoading | 117 | voltage loading | DSP | external, prompt
|  | bit 5 |  | 118 |  | DSP
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 | SpdFail(DC) | 121 | Lightning protection fault (DC) | DSP | external, prompt | shutdown
|  | bit 1 | SpdFail(AC) | 122 | Lightning protection fault (AC) | DSP | external, prompt
|  | bit 2 |  | 123
|  | bit 3 | BatDchgProhibit | 124 | Battery forbidden discharge protection | DSP | external, prompt
|  | bit 4 | BatLowVoltShut | 125 | Low battery shutdown | DSP | external, prompt
|  | bit 5 |  | 126 | Low battery pre-alarm
|  | bit 6 |  | 127
|  | bit 7 |  | 128
Fault9 | byte 0 | bit 0 | PermHwAcOCP | 129 | AC hardware overcurrent fault | DSP | external | permanent
|  | bit 1 | PermBusOVP | 130 | BusOvervoltage fault | DSP | external
|  | bit 2 | PermHwBusOVP | 131 | BusHardware overvoltage fault | DSP | external
|  | bit 3 | PermIpvUnbalance | 132 | PVUnbalanced current failure | DSP | external
|  | bit 4 | PermEPSBatOCP | 133 | EPSBattery overcurrent fault | DSP | external
|  | bit 5 | PermAcOCPINstant | 134 | Output transient overcurrent fault | DSP | external
|  | bit 6 | PermIacUnbalance | 135 | AC current unbalance fault | DSP | external
|  | bit 7 | PermInvStartFail | 136 | Inverter soft start failure fault
| byte 1 | bit 0 | PermInCfgError | 137 | Input mode setting failure | DSP | external
|  | bit 1 | PermDCOCPInstant | 138 | Input overcurrent fault | DSP | external
|  | bit 2 | PermHwDCOCP | 139 | Input hardware overcurrent fault | DSP | external
|  | bit 3 | PermRelayFail | 140 | Permanent failure of the relay | DSP | external
|  | bit 4 | PermBusUnbalance | 141 | Bus unbalance fault | DSP | external
|  | bit 5 | PermSpdFail(DC) | 142 | Lightning protection fault (DC) | DSP
|  | bit 6 | PermSpdFail(AC) | 143 | Lightning protection fault (AC) | DSP
|  | bit 7 | PermGridRlyFail | 144 | Grid relay failure
Fault10 | byte 0 | bit 0 | USBFault | 145 | USBFault | ARM |  | communication board
|  | bit 1 | WifiFault | 146 | WIFIFault | ARM
|  | bit 2 | BluetoothFault | 147 | bluetooth malfunction | ARM
|  | bit 3 | RTCFault | 148 | RTCclock failure | ARM
|  | bit 4 | CommEEPROMFault | 149 | communication boardEEPROMmistake | ARM
|  | bit 5 | FlashFault | 150 | Communication board FLASH error | ARM
|  | bit 6 |  | 151
|  | bit 7 | SafetyVerFault | 152 | wrong safety version | ARM | external
| byte 1 | bit 0 | SCILose(DC) | 153 | SCI Error (DC) | ARM
|  | bit 1 | SCILose(AC) | 154 | SCI Error (AC) | ARM
|  | bit 2 | SCILose(Fuse) | 155 | SCI error (Fuse) | ARM
|  | bit 3 | SoftVerError | 156 | Inconsistent software version | ARM | external
|  | bit 4 | BMS1CommFault | 157 | Lithium battery 1 communication failure | ARM | external
|  | bit 5 | BMS2CommFault | 158 | Lithium battery 2 communication failure | ARM | external
|  | bit 6 | BMS3CommFault | 159 | Lithium battery 3 communication failure | ARM | external
|  | bit 7 | BMS4CommFault | 160 | Lithium battery 4 communication failure | ARM | external
Fault11 | byte 0 | bit 0 | ForceShutdown | 161 | Force shutdown | ARM | external | Shutdown and load reduction of communication board
|  | bit 1 | RemoteShutdown | 162 | Remote shutdown | ARM | external
|  | bit 2 | Drms0Shutdown | 163 | Drms0 shutdown | ARM | external
|  | bit 3 | PSCommFault | 164 | Power station communication failure shutdown
|  | bit 4 | RemoteDerating | 165 | remote load shedding | ARM | external
|  | bit 5 | LogicIfDerating | 166 | Logical interface load shedding | ARM | external
|  | bit 6 | AlarmAntiReflux | 167 | Anti-reverse flow and load reduction | ARM | external
|  | bit 7 |  | 168
| byte 1 | bit 0 | FanFault1 | 169 | fan1Fault | ARM | external | peripheral components
|  | bit 1 | FanFault2 | 170 | fan2Fault | ARM | external
|  | bit 2 | FanFault3 | 171 | fan3Fault | ARM | external
|  | bit 3 | FanFault4 | 172 | fan4Fault | ARM | external
|  | bit 4 | FanFault5 | 173 | fan5Fault | ARM | external
|  | bit 5 | FanFault6 | 174 | fan6Fault | ARM | external
|  | bit 6 | FanFault7 | 175 | fan7Fault | ARM | external
|  | bit 7 | MeterCommLose | 176 | Electricity meter communication failure | ARM | external
Fault12 | byte 0 | bit 0 | BMS OVP | 177 | BMSOvervoltage protection | BMS | external, prompt | BMS
|  | bit 1 | BMS UVP | 178 | BMSUndervoltage protection | BMS | external, prompt
|  | bit 2 | BMS OTP | 179 | BMSHigh temperature protection | BMS | external, prompt
|  | bit 3 | BMS UTP | 180 | BMScryogenic protection | BMS | external, prompt
|  | bit 4 | BMS OCP | 181 | BMSOvercurrent Protection | BMS | external, prompt
|  | bit 5 | BMS Short | 182 | BMSShort circuit protection | BMS | external, prompt
|  | bit 6 | BMS VerFault | 183 | BMSInconsistent version | ARM | external, prompt
|  | bit 7 | BMS CAN VerFault | 184 | BMSCANInconsistent version | ARM | external, prompt
| byte 1 | bit 0 | BMS CAN VerLow | 185 | BMS CANThe version is too low | ARM | external, prompt
|  | bit 1 |  | 186
|  | bit 2 |  | 187
|  | bit 3 |  | 188
|  | bit 4 | AFCICommLose | 189 | Arc device communication failure | ARM | external, prompt
|  | bit 5 | DCArcingAlarm | 190 | DC arc alarm | ARM
|  | bit 6 | PID_Output_Fail | 191 | PIDRepair failed | ARM
|  | bit 7 | PLC_Com_Fail | 192 | PLCModule heartbeat lost
Fault13 | byte 0 | bit 0 | StrFuseALM1-1 | 193 | String fuse open circuit 1-1 | FUSE |  | FUSE
|  | bit 1 | StrFuseALM1-2 | 194 | String fuse open circuit 1-2 | FUSE
|  | bit 2 | StrFuseALM2-1 | 195 | String fuse open circuit 2-1 | FUSE
|  | bit 3 | StrFuseALM2-2 | 196 | String fuse open circuit 2-2 | FUSE
|  | bit 4 | StrFuseALM3-1 | 197 | String fuse open circuit 3-1 | FUSE
|  | bit 5 | StrFuseALM3-2 | 198 | String fuse open circuit 3-2 | FUSE
|  | bit 6 | StrFuseALM4-1 | 199 | String fuse open circuit 4-1 | FUSE
|  | bit 7 | StrFuseALM4-2 | 200 | String fuse open circuit 4-2 | FUSE
| byte 1 | bit 0 | StrFuseALM5-1 | 201 | String fuse open circuit 5-1 | FUSE
|  | bit 1 | StrFuseALM5-2 | 202 | String fuse open circuit 5-2 | FUSE
|  | bit 2 | StrFuseALM6-1 | 203 | String fuse open circuit 6-1 | FUSE
|  | bit 3 | StrFuseALM6-2 | 204 | String fuse open circuit 6-2 | FUSE
|  | bit 4 | StrFuseALM7-1 | 205 | String fuse open circuit 7-1 | FUSE
|  | bit 5 | StrFuseALM7-2 | 206 | String fuse open circuit 7-2 | FUSE
|  | bit 6 | StrFuseALM8-1 | 207 | String fuse open circuit 8-1 | FUSE
|  | bit 7 | StrFuseALM8-2 | 208 | String fuse open circuit 8-2 | FUSE
Fault14 | byte 0 | bit 0 | StrFuseALM9-1 | 209 | String fuse open 9-1 | FUSE
|  | bit 1 | StrFuseALM9-2 | 210 | String fuse open 9-2 | FUSE
|  | bit 2 | StrFuseALM10-1 | 211 | String fuse open circuit 10-1 | FUSE
|  | bit 3 | StrFuseALM10-2 | 212 | String fuse open circuit 10-2 | FUSE
|  | bit 4 | StrFuseALM11-1 | 213 | String fuse open circuit 11-1 | FUSE
|  | bit 5 | StrFuseALM11-2 | 214 | String fuse open circuit 11-2 | FUSE
|  | bit 6 | StrFuseALM12-1 | 215 | String fuse open circuit 12-1 | FUSE
|  | bit 7 | StrFuseALM12-2 | 216 | String fuse open circuit 12-2 | FUSE
| byte 1 | bit 0 | StrFuseALM13-1 | 217 | String fuse open circuit 13-1 | FUSE
|  | bit 1 | StrFuseALM13-2 | 218 | String fuse open circuit 13-2 | FUSE
|  | bit 2 | StrFuseALM14-1 | 219 | String fuse open circuit 14-1 | FUSE
|  | bit 3 | StrFuseALM14-2 | 220 | String fuse open circuit 14-2 | FUSE
|  | bit 4 | StrFuseALM15-1 | 221 | String fuse open circuit 15-1 | FUSE
|  | bit 5 | StrFuseALM15-2 | 222 | String fuse open circuit 15-2 | FUSE
|  | bit 6 | StrFuseALM16-1 | 223 | String fuse open circuit 16-1 | FUSE
|  | bit 7 | StrFuseALM16-2 | 224 | String fuse open circuit 16-2 | FUSE
Fault15 | byte 0 | bit 0 | InputFuseALM0 | 225 | Input fuse open 0 | FUSE
|  | bit 1 | InputFuseALM1 | 226 | Input fuse open 1 | FUSE
|  | bit 2 | InputFuseALM2 | 227 | Input fuse open 2 | FUSE
|  | bit 3 | InputFuseALM3 | 228 | Input fuse open 3 | FUSE
|  | bit 4 | InputFuseALM4 | 229 | Input fuse open 4 | FUSE
|  | bit 5 | InputFuseALM5 | 230 | Input fuse open 5 | FUSE
|  | bit 6 | InputFuseALM6 | 231 | Input fuse open 6 | FUSE
|  | bit 7 | InputFuseALM7 | 232 | Input fuse open 7 | FUSE
| byte 1 | bit 0 | InputFuseALM8 | 233 | Input fuse open circuit 8 | FUSE
|  | bit 1 | InputFuseALM9 | 234 | Input fuse open 9 | FUSE
|  | bit 2 | InputFuseALM10 | 235 | Input fuse open 10 | FUSE
|  | bit 3 | InputFuseALM11 | 236 | Input fuse open 11 | FUSE
|  | bit 4 | InputFuseALM12 | 237 | Input fuse open 12 | FUSE
|  | bit 5 | InputFuseALM13 | 238 | Input fuse open 13 | FUSE
|  | bit 6 | InputFuseALM14 | 239 | Input fuse open 14 | FUSE
|  | bit 7 | InputFuseALM15 | 240 | Input fuse open 15 | FUSE
Fault16 | byte 0 | bit 0 | CombinerOVGp1 | 241 |  |  |  | Confluence
|  | bit 1 | CombinerOVGp2 | 242
|  | bit 2 | CombinerOVGp3 | 243
|  | bit 3 | CombinerOVGp4 | 244
|  | bit 4 | CombinerOVGp5 | 245
|  | bit 5 | CombinerOVGp6 | 246
|  | bit 6 | CombinerOVGp7 | 247
|  | bit 7 | CombinerOVGp8 | 248
| byte 1 | bit 0 | CombinerOVGp9 | 249
|  | bit 1 | CombinerOVGp10 | 250
|  | bit 2 | CombinerOVGp11 | 251
|  | bit 3 | CombinerOVGp12 | 252
|  | bit 4 | CombinerOVGp13 | 253
|  | bit 5 | CombinerOVGp14 | 254
|  | bit 6 | CombinerOVGp15 | 255
|  | bit 7 | CombinerOVGp16 | 256
Fault17 | byte 0 | bit 0 | CombinerUVGp1 | 257 |  |  |  | Confluence
|  | bit 1 | CombinerUVGp2 | 258
|  | bit 2 | CombinerUVGp3 | 259
|  | bit 3 | CombinerUVGp4 | 260
|  | bit 4 | CombinerUVGp5 | 261
|  | bit 5 | CombinerUVGp6 | 262
|  | bit 6 | CombinerUVGp7 | 263
|  | bit 7 | CombinerUVGp8 | 264
| byte 1 | bit 0 | CombinerUVGp9 | 265
|  | bit 1 | CombinerUVGp10 | 266
|  | bit 2 | CombinerUVGp11 | 267
|  | bit 3 | CombinerUVGp12 | 268
|  | bit 4 | CombinerUVGp13 | 269
|  | bit 5 | CombinerUVGp14 | 270
|  | bit 6 | CombinerUVGp15 | 271
|  | bit 7 | CombinerUVGp16 | 272
Fault18 | byte 0 | bit 0 | CombinerOC1 | 273 |  |  |  | Confluence
|  | bit 1 | CombinerOC2 | 274
|  | bit 2 | CombinerOC3 | 275
|  | bit 3 | CombinerOC4 | 276
|  | bit 4 | CombinerOC5 | 277
|  | bit 5 | CombinerOC6 | 278
|  | bit 6 | CombinerOC7 | 279
|  | bit 7 | CombinerOC8 | 280
| byte 1 | bit 0 | CombinerOC9 | 281
|  | bit 1 | CombinerOC10 | 282
|  | bit 2 | CombinerOC11 | 283
|  | bit 3 | CombinerOC12 | 284
|  | bit 4 | CombinerOC13 | 285
|  | bit 5 | CombinerOC14 | 286
|  | bit 6 | CombinerOC15 | 287
|  | bit 7 | CombinerOC16 | 288
Fault19 | byte 0 | bit 0 | CombinerOC17 | 289 |  |  |  | Confluence
|  | bit 1 | CombinerOC18 | 290
|  | bit 2 | CombinerOC19 | 291
|  | bit 3 | CombinerOC20 | 292
|  | bit 4 | CombinerOC21 | 293
|  | bit 5 | CombinerOC22 | 294
|  | bit 6 | CombinerOC23 | 295
|  | bit 7 | CombinerOC24 | 296
| byte 1 | bit 0 | CombinerOC25 | 297
|  | bit 1 | CombinerOC26 | 298
|  | bit 2 | CombinerOC27 | 299
|  | bit 3 | CombinerOC28 | 300
|  | bit 4 | CombinerOC29 | 301
|  | bit 5 | CombinerOC30 | 302
|  | bit 6 | CombinerOC31 | 303
|  | bit 7 | CombinerOC32 | 304
Fault20 | byte 0 | bit 0 |  | 305 |  |  |  | Confluence
|  | bit 1 |  | 306
|  | bit 2 |  | 307
|  | bit 3 |  | 308
|  | bit 4 |  | 309
|  | bit 5 |  | 310
|  | bit 6 |  | 311
|  | bit 7 |  | 312
| byte 1 | bit 0 |  | 313
|  | bit 1 |  | 314
|  | bit 2 |  | 315
|  | bit 3 |  | 316
|  | bit 4 |  | 317
|  | bit 5 |  | 318
|  | bit 6 |  | 319
|  | bit 7 |  | 320
Fault21 | byte 0 | bit 0 |  | 321 |  |  |  | Confluence
|  | bit 1 |  | 322
|  | bit 2 |  | 323
|  | bit 3 |  | 324
|  | bit 4 |  | 325
|  | bit 5 |  | 326
|  | bit 6 |  | 327
|  | bit 7 |  | 328
| byte 1 | bit 0 |  | 329
|  | bit 1 |  | 330
|  | bit 2 |  | 331
|  | bit 3 |  | 332
|  | bit 4 |  | 333
|  | bit 5 |  | 334
|  | bit 6 |  | 335
|  | bit 7 |  | 336
Fault22 | byte 0 | bit 0 | CombinerRefluxFault1 | 337 |  |  |  | Confluence
|  | bit 1 | CombinerRefluxFault2 | 338
|  | bit 2 | CombinerRefluxFault3 | 339
|  | bit 3 | CombinerRefluxFault4 | 340
|  | bit 4 | CombinerRefluxFault5 | 341
|  | bit 5 | CombinerRefluxFault6 | 342
|  | bit 6 | CombinerRefluxFault7 | 343
|  | bit 7 | CombinerRefluxFault8 | 344
| byte 1 | bit 0 | CombinerRefluxFault9 | 345
|  | bit 1 | CombinerRefluxFault10 | 346
|  | bit 2 | CombinerRefluxFault11 | 347
|  | bit 3 | CombinerRefluxFault12 | 348
|  | bit 4 | CombinerRefluxFault13 | 349
|  | bit 5 | CombinerRefluxFault14 | 350
|  | bit 6 | CombinerRefluxFault15 | 351
|  | bit 7 | CombinerRefluxFault16 | 352
Fault23 | byte 0 | bit 0 | CombinerRefluxFault17 | 353 |  |  |  | Confluence
|  | bit 1 | CombinerRefluxFault18 | 354
|  | bit 2 | CombinerRefluxFault19 | 355
|  | bit 3 | CombinerRefluxFault20 | 356
|  | bit 4 | CombinerRefluxFault21 | 357
|  | bit 5 | CombinerRefluxFault22 | 358
|  | bit 6 | CombinerRefluxFault23 | 359
|  | bit 7 | CombinerRefluxFault24 | 360
| byte 1 | bit 0 | CombinerRefluxFault25 | 361
|  | bit 1 | CombinerRefluxFault26 | 362
|  | bit 2 | CombinerRefluxFault27 | 363
|  | bit 3 | CombinerRefluxFault28 | 364
|  | bit 4 | CombinerRefluxFault29 | 365
|  | bit 5 | CombinerRefluxFault30 | 366
|  | bit 6 | CombinerRefluxFault31 | 367
|  | bit 7 | CombinerRefluxFault32 | 368
Fault24 | byte 0 | bit 0 |  | 369 |  |  |  | Confluence
|  | bit 1 |  | 370
|  | bit 2 |  | 371
|  | bit 3 |  | 372
|  | bit 4 |  | 373
|  | bit 5 |  | 374
|  | bit 6 |  | 375
|  | bit 7 |  | 376
| byte 1 | bit 0 |  | 377
|  | bit 1 |  | 378
|  | bit 2 |  | 379
|  | bit 3 |  | 380
|  | bit 4 |  | 381
|  | bit 5 |  | 382
|  | bit 6 |  | 383
|  | bit 7 |  | 384
Fault25 | byte 0 | bit 0 |  | 385 |  |  |  | Confluence
|  | bit 1 |  | 386
|  | bit 2 |  | 387
|  | bit 3 |  | 388
|  | bit 4 |  | 389
|  | bit 5 |  | 390
|  | bit 6 |  | 391
|  | bit 7 |  | 392
| byte 1 | bit 0 |  | 393
|  | bit 1 |  | 394
|  | bit 2 |  | 395
|  | bit 3 |  | 396
|  | bit 4 |  | 397
|  | bit 5 |  | 398
|  | bit 6 |  | 399
|  | bit 7 |  | 400
Fault26 | byte 0 | bit 0 | AFCI0 | 401 | arc fault |  |  | arc
|  | bit 1 | AFCI1 | 402 | arc fault
|  | bit 2 | AFCI2 | 403 | arc fault
|  | bit 3 | AFCI3 | 404 | arc fault
|  | bit 4 | AFCI4 | 405 | arc fault
|  | bit 5 | AFCI5 | 406 | arc fault
|  | bit 6 | AFCI6 | 407 | arc fault
|  | bit 7 | AFCI7 | 408 | arc fault
| byte 1 | bit 0 | AFCI8 | 409 | arc fault
|  | bit 1 | AFCI9 | 410 | arc fault
|  | bit 2 | AFCI10 | 411 | arc fault
|  | bit 3 | AFCI11 | 412 | arc fault
|  | bit 4 | AFCI12 | 413 | arc fault
|  | bit 5 | AFCI13 | 414 | arc fault
|  | bit 6 | AFCI14 | 415 | arc fault
|  | bit 7 | AFCI15 | 416 | arc fault
Fault27 | byte 0 | bit 0 | AFCI16 | 417 | arc fault |  |  | arc
|  | bit 1 | AFCI17 | 418 | arc fault
|  | bit 2 | AFCI18 | 419 | arc fault
|  | bit 3 | AFCI19 | 420 | arc fault
|  | bit 4 | AFCI20 | 421 | arc fault
|  | bit 5 | AFCI21 | 422 | arc fault
|  | bit 6 | AFCI22 | 423 | arc fault
|  | bit 7 | AFCI23 | 424 | arc fault
| byte 1 | bit 0 | AFCI24 | 425 | arc fault
|  | bit 1 | AFCI25 | 426 | arc fault
|  | bit 2 | AFCI26 | 427 | arc fault
|  | bit 3 | AFCI27 | 428 | arc fault
|  | bit 4 | AFCI28 | 429 | arc fault
|  | bit 5 | AFCI29 | 430 | arc fault
|  | bit 6 | AFCI30 | 431 | arc fault
|  | bit 7 | AFCI31 | 432 | arc fault
Fault28 | byte 0 | bit 0 |  | 433 |  | Protocol version error (ARM) |  | wrong protocol version(ARM)
|  | bit 1 |  | 434
|  | bit 2 |  | 435
|  | bit 3 |  | 436
|  | bit 4 |  | 437
|  | bit 5 |  | 438
|  | bit 6 |  | 439
|  | bit 7 |  | 440
| byte 1 | bit 0 |  | 441
|  | bit 1 |  | 442
|  | bit 2 |  | 443
|  | bit 3 |  | 444
|  | bit 4 |  | 445
|  | bit 5 |  | 446
|  | bit 6 |  | 447
|  | bit 7 |  | 448
Fault29 | byte 0 | bit 0 | VGridNPEOver | 449 | Neutral ground voltage is too high | grid |  | grid
|  | bit 1 | SwPvBranchOCP | 450 | PVBranch software overcurrent
|  | bit 2 |  | 451
|  | bit 3 |  | 452
|  | bit 4 |  | 453
|  | bit 5 |  | 454
|  | bit 6 |  | 455
|  | bit 7 |  | 456
| byte 1 | bit 0 |  | 457
|  | bit 1 |  | 458
|  | bit 2 |  | 459
|  | bit 3 |  | 460
|  | bit 4 |  | 461
|  | bit 5 |  | 462
|  | bit 6 |  | 463
|  | bit 7 | This bit disables | 464
Fault30 | byte 0 | bit 0 |  | 465 |  | grid |  | grid
|  | bit 1 |  | 466
|  | bit 2 |  | 467
|  | bit 3 |  | 468
|  | bit 4 |  | 469
|  | bit 5 |  | 470
|  | bit 6 |  | 471
|  | bit 7 |  | 472
| byte 1 | bit 0 |  | 473
|  | bit 1 |  | 474
|  | bit 2 |  | 475
|  | bit 3 |  | 476
|  | bit 4 |  | 477
|  | bit 5 |  | 478
|  | bit 6 |  | 479
|  | bit 7 | This bit disables | 480

## Status Information Table
Table | Byte | Bit | bit field | Numbering | Remark
State1 | byte 0 | bit 0 |  | 001 | Grid low voltage drop load
|  | bit 1 |  | 002 | Over temperature derating
|  | bit 2 |  | 003 | Busbar overvoltage drop load
|  | bit 3 |  | 004 | Reactive power limited active power
|  | bit 4 |  | 005 | Command active load shedding
|  | bit 5 |  | 006 | DRMs offload
|  | bit 6 |  | 007 | Anti-reverse flow and load reduction
|  | bit 7 |  | 008 | Remote Active Control
| byte 1 | bit 0 |  | 009 | Over voltage drop load
|  | bit 1 |  | 010 | Over frequency load reduction
|  | bit 2 |  | 011 | underfrequency loading
|  | bit 3 |  | 012 | Internal derating
|  | bit 4 |  | 013
|  | bit 5 |  | 014
|  | bit 6 |  | 015
|  | bit 7 |  | 016
State2 | byte 0 | bit 0 |  | 017 | Remote PF Control
|  | bit 1 |  | 018 | Remote reactive power control
|  | bit 2 |  | 019 | Independent reactive power control
|  | bit 3 |  | 020
|  | bit 4 |  | 021
|  | bit 5 |  | 022
|  | bit 6 |  | 023
|  | bit 7 |  | 024
| 0 | bit 0 |  | 025 | Force shutdown
|  | bit 1 |  | 026 | Remote shutdown
|  | bit 2 |  | 027 | DRMs0 shutdown
|  | bit 3 |  | 028
|  | bit 4 |  | 029
|  | bit 5 |  | 030
|  | bit 6 |  | 031
|  | bit 7 |  | 032
State3 | byte 0 | bit 0 |  | 033
|  | bit 1 |  | 034
|  | bit 2 |  | 035
|  | bit 3 |  | 036
|  | bit 4 |  | 037
|  | bit 5 |  | 038
|  | bit 6 |  | 039
|  | bit 7 |  | 040
| byte 1 | bit 0 |  | 041
|  | bit 1 |  | 042
|  | bit 2 |  | 043
|  | bit 3 |  | 044
|  | bit 4 |  | 045
|  | bit 5 |  | 046
|  | bit 6 |  | 047
|  | bit 7 |  | 048
State4 | byte 0 | bit 0 |  | 049
|  | bit 1 |  | 050
|  | bit 2 |  | 051
|  | bit 3 |  | 052
|  | bit 4 |  | 053
|  | bit 5 |  | 054
|  | bit 6 |  | 055
|  | bit 7 |  | 056
| byte 1 | bit 0 |  | 057
|  | bit 1 |  | 058
|  | bit 2 |  | 059
|  | bit 3 |  | 060
|  | bit 4 |  | 061
|  | bit 5 |  | 062
|  | bit 6 |  | 063
|  | bit 7 |  | 064
State5 | byte 0 | bit 0 |  | 065
|  | bit 1 |  | 066
|  | bit 2 |  | 067
|  | bit 3 |  | 068
|  | bit 4 |  | 069
|  | bit 5 |  | 070
|  | bit 6 |  | 071
|  | bit 7 |  | 072
| byte 1 | bit 0 |  | 073
|  | bit 1 |  | 074
|  | bit 2 |  | 075
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
State6 | byte 0 | bit 0 | RemoteDerating | 081 | Remote load drop enable
|  | bit 1 | LogicIfDerating | 082 | Logical interface load shedding enable
|  | bit 2 | AlarmAntiReflux | 083 | Anti-reverse flow and load reduction enable
|  | bit 3 |  | 084
|  | bit 4 |  | 085
|  | bit 5 |  | 086
|  | bit 6 |  | 087
|  | bit 7 |  | 088
| byte 1 | bit 0 |  | 089
|  | bit 1 |  | 090
|  | bit 2 |  | 091
|  | bit 3 |  | 092
|  | bit 4 |  | 093
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
State7 | byte 0 | bit 0 |  | 097
|  | bit 1 |  | 098
|  | bit 2 |  | 099
|  | bit 3 |  | 100
|  | bit 4 |  | 101
|  | bit 5 |  | 102
|  | bit 6 |  | 103
|  | bit 7 |  | 104
| byte 1 | bit 0 |  | 105
|  | bit 1 |  | 106
|  | bit 2 |  | 107
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 |  | 110
|  | bit 6 |  | 111
|  | bit 7 |  | 112
State8 | byte 0 | bit 0 |  | 113
|  | bit 1 |  | 114
|  | bit 2 |  | 115
|  | bit 3 |  | 116
|  | bit 4 |  | 117
|  | bit 5 |  | 118
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 |  | 121
|  | bit 1 |  | 122
|  | bit 2 |  | 123
|  | bit 3 |  | 124
|  | bit 4 |  | 125
|  | bit 5 |  | 126
|  | bit 6 |  | 127
|  | bit 7 |  | 128
State9 | byte 0 | bit 0 |  | 129
|  | bit 1 |  | 130
|  | bit 2 |  | 131
|  | bit 3 |  | 132
|  | bit 4 |  | 133
|  | bit 5 |  | 134
|  | bit 6 |  | 135
|  | bit 7 |  | 136
| byte 1 | bit 0 |  | 137
|  | bit 1 |  | 138
|  | bit 2 |  | 139
|  | bit 3 |  | 140
|  | bit 4 |  | 141
|  | bit 5 |  | 142
|  | bit 6 |  | 143
|  | bit 7 |  | 144

## PCU Fault Bit Description
Warning1 | bit | ID | Fault | Notes
| 0 | 800
| 1 | 801 | IschgSoftStartFail | Charging soft start failed
| 2 | 802 | IsdchgSoftStartFail | Discharge soft start failed
| 3 | 803 | Fan1Fault | Fan 1 failure
| 4 | 804 | Fan2Fault | Fan 2 failure
| 5 | 805 | Fan3Fault | Fan 3 failure
| 6 | 806 | Fan4Fault | Fan 4 failure
| 7 | 807 | PCU VerFault | Inconsistent PCU versions
| 8 | 808 | HS1HighTempWarning | Radiator 1 over temperature alarm
| 9 | 809 | EnvHighTempWarning | Ambient temperature over temperature alarm
| 10 | 810 | HS2HighTempWarning | Radiator 2 over temperature alarm
| 11 | 811
| 12 | 812
| 13 | 813 | StopChgWarning | Disable charging alarm
| 14 | 814 | StopDchgWarning | Discharge warning
| 15 | 815 | BatUnbalancedWarning | Battery imbalance alarm
Warning2 | 0 | 816 | BusAvgOVWarning | Bus overvoltage alarm
| 1 | 817 | BusAvgUVWarning | Bus undervoltage alarm
| 2 | 818 | BatAvgOVWarning | Battery overvoltage alarm
| 3 | 819 | BatAvgUVWarning | Battery undervoltage alarm
| 4 | 820
| 5 | 821
| 6 | 822
| 7 | 823
| 8 | 824
| 9 | 825
| 11 | 827
| 12 | 828
| 13 | 829
| 14 | 830
| 15 | 831
Warning3 | 0 | 832
| 1 | 833
| 2 | 834
| 3 | 835
| 4 | 836
| 5 | 837
| 6 | 838
| 7 | 839
| 8 | 840
| 9 | 841
| 10 | 842
| 11 | 843
| 12 | 844
| 13 | 845
Warning4 | 0 | 848
| 1 | 849
| 2 | 850
| 3 | 851
| 4 | 852
| 5 | 853
| 6 | 854
| 7 | 855
| 8 | 856
| 9 | 857
| 10 | 858
| 11 | 859
| 12 | 860
| 13 | 861
| 14 | 862
| 15 | 863
Fault1 | 0 | 864 | HS1OverTempFault | Heatsink 1 over temperature protection
| 1 | 865 | OverTempFault_Env | Ambient temperature over temperature protection
| 2 | 866 | SciCommFault | Sci communication failure
| 3 | 867 | Can1CommFault | Can1 communication failure
| 4 | 868 | Relay1Fail | Relay 1 fault
| 5 | 869 | HS2OverTempFault | Heatsink 2 over temperature protection
| 6 | 870 | Can2CommFault | Can2 communication failure
| 7 | 871 | Relay2Fail | Relay 2 fault
| 8 | 872 | SwBusInstantOVP | Bus software overvoltage
| 9 | 873 | SwBusInstantUVP | Bus software undervoltage
| 10 | 874 | SwBatInstantOVP | Battery software overvoltage
| 11 | 875 | SwBatInstantUVP | Battery software undervoltage
| 12 | 876 | SwBatInstantOCP | Battery software overcurrent
| 13 | 877 | FlyingCap1OVP | Flying capacitor 1 overvoltage
| 14 | 878 | FlyingCap2OVP | Flying capacitor 2 overvoltage
| 15 | 879 | HwOCP | hardware overcurrent
Fault2 | 0 | 880 | unrecoverBusAvgOV | Permanent busbar overvoltage
| 1 | 881 | unrecoverBatAvgUV | Permanent battery undervoltage
| 2 | 882 | unrecoverOCPInstant | permanent overcurrent
| 3 | 883 | unrecoverHwOCP | Permanent hardware overcurrent
| 4 | 884 | FlyingCap3OVP | Flying capacitor 3 overvoltage
| 5 | 885 | FlyingCap4OVP | Flying capacitor 4 overvoltage
| 6 | 886 | FlyingCap1UVP | Flying capacitor 1 undervoltage
| 7 | 887 | FlyingCap2UVP | Flying capacitor 2 undervoltage
| 8 | 888 | unrecoverRelay1Fail | Relay 1 permanent fault
| 9 | 889 | unrecoverRelay2Fail | Relay 2 permanent fault
| 10 | 890 | FlyingCap3UVP | Flying capacitor 3 undervoltage
| 11 | 891 | FlyingCap4UVP | Flying capacitor 4 undervoltage
| 12 | 892
| 13 | 893
| 14 | 894
| 15 | 895
| 13 | 893
| 14 | 894 | unrecoverBatActFail | Permanent battery activation failed
| 15 | 895 | unrecoverBusRPP | Permanent BUS reverse connection
Fault3 | 0 | 896 | BatteryStateErr | battery status error
| 1 | 897 | PWMModeErr | PWM mode error
| 2 | 898 | BMSVerionErr | BMS version error
| 3 | 899 | BMSOVOCP | BMS overvoltage and overcurrent fault
| 4 | 900 | SwBatAvgOCP | Battery Average Over Current Protection
| 5 | 901 | SwAvgOverloadP | Average value overload protection
| 6 | 902 | SwBusInstantOCP | Bus software overcurrent
| 7 | 903 | SwCBCOCP | Software CBC overcurrent protection
| 8 | 904 | PackIDErr | PackIDmistake
| 9 | 905
| 10 | 906
| 11 | 907
| 12 | 908
| 13 | 909
| 14 | 910
| 15 | 911
Fault4 | 0 | 912
| 1 | 913
| 2 | 914
| 3 | 915
| 4 | 916
| 5 | 917
| 6 | 918
| 7 | 919
| 8 | 920
| 9 | 921
| 10 | 922
| 11 | 923
| 12 | 924
| 13 | 925
| 14 | 926
| 15 | 927

## BDU Fault Information
Fault1 | bit | ID | Fault | Notes
| 0 | 928 | battery reversed
| 1 | 929 | Fusing fault
| 2 | 930
| 3 | 931
| 4 | 932
| 5 | 933
| 6 | 934
| 7 | 935
| 8 | 936
| 9 | 937
| 10 | 938
| 11 | 939
| 12 | 940
| 13 | 941
| 14 | 942
| 15 | 943

## Version Update Record
Modified date | address | Modify the description
2020-05-23 | 0x0940 | IncreaseBit4
| 0x0404 | Increase2new state description
| 0x09C0 | IncreaseBit3
| 0x09DB-0x09DE | Add parameters
| 0x2006 | Update value definition description
2020-06-03 | 0x102D | newCTAuto Calibration Register
2020-06-10 | 0x0940 | IncreaseBit5
2020-06-29 | 0x0914-0x0915 | Add parameters
| Fault2-byte1-bit6 | Add fault
| Fault3-byte1-bit6 | Add fault
2020-08-31 | 0x1046 | Add battery protocol type
| 0x1038 | Add address
| 0xA07C-0xA07F | Add address
| Fault3-byte0-bit5 | Add InverterSoftStartFail
| Fault3-byte1-bit7 | Add SNTypeFault
| Fault9-byte1-bit5 | Increase unrecoverSpdFail(DC)
| Fault9-byte1-bit6 | Add unrecoverSpdFail(AC)
| Fault2-byte0-bit1 | Modify fault name
| Fault2-byte1-bit0 | Increase HwADFaultDCI(DC)
| Fault2-byte1-bit1 | Added HwADFaultIdcBranch
| Fault10-byte1-bit4 | Modify fault name
| Fault10-byte1-bit5 | Added BMS2CommunicatonFault
| Fault10-byte1-bit6 | Added BMS3CommunicatonFault
| Fault10-byte1-bit7 | Added BMS4CommunicatonFault
| Fault10-byte0-bit7 | Increase SafetyVerFault
2020-09-04 | 0x803C-0x803F | Add address
| 0x9000-0x9FFF | Added BMS transparent transmission area
| 0x06D1-0x06E2 | Add address
| Fault5-byte1-bit1 | Added FlyingCapOVP
2020-10-13 | 0x08C8-0x08CC | Add safety parameters
| 0x0A04-0x0A05 | Add safety parameters
| 0x1050 | Voltage accuracy issue fix
2020-10-30 | 0x9000-0x9FFF | Newly added package ID in the real-time data part of the BMS transparent transmission area
| 0x4B0-0x4B9 | Add address
| 0x522-0x527 | Add address
| Fault11-byte1-bit7 | add fault
2020-11-16 | 0x1039-0x103D | Add address
2020-12-02 | 0x0901,0x0A03 | The original address value range is updated
| 0x1046 | The original address value range is updated
| 0x1052 | Add battery parameter address
| 0x1054-0x1056 | Add battery parameter address
| 0x1023 | The original address value range is updated
| 0x1024 | Original address unit update
| 0x1084-0x108C | Add arc configuration address
| 0xA070-0xA075 | Add address
| 0x0780-0x07BF | Add arc real-time information area
| 0x2007-0x200B | Add the name and address of the safety country
| 0x0432-0x043A | Add fault information address
| Fault6-byte1-bit0 | Increase SwPvOCP
| Fault26/27 | Added AFCI fault
2021-01-27 | 0x9005 | date register type bug fix
| 0x9051-0x906A, 0x9079, 0x9091-0x90AA, 0x90B4 | Accuracy change
| 0x907A | Add address
| 0x1105-0x110B | Add address
| 0x04BA-0x04BC | Add address
| 0x108D-0x108E | Add address
| Fault11-byte1-bit6 | Added FanFault7
| Fault12-byte0-bit6 | Added BMS VerFault
| Fault12-byte0-bit7 | Added BMS CAN VerFault
| Fault12-byte1-bit0 | Added BMS CAN VerLow
| Fault12-byte1-bit4 | Added AFCICommLose
| Fault12-byte1-bit5 | Added DCArcingAlarmFault
2021-02-05 | Fault7-byte1-bit0 | Added MeterCommFault
2021-02-16 | 0x118D-0x1190, 0x1197-0x119A, 0x11A1-0x11A4 | data type update
| 0x1035 | Update register value range and value definition
| Fault6-byte1-bit1 | newIbalanceOCP
| 0x1024 | fix precision issues
2021-03-16 | Fault1-byte1-bit3 | field name correction
| Fault1-byte1-bit4 | Added anti-reverse current overload fault
| Fault8-byte1-bit3 | field name correction
| 0x460-0x465 | Added safety version number register
| 0x0951-0x0960 | Added safety parameter address
| 0x0980 | Add a new bit field definition to the original address
| 0x0981 | Maximum and minimum corrections, please see the comments
| 0x0982 | Maximum and minimum correction
| 0x0993 | Original address field, unit, remarks updated
| 0x0995 | Original address and location, remarks updated
| 0x0996 | Original address field, type, remarks updated
| 0x09A1 | Added safety parameter address
| 0x09C0 | Add a new bit field definition to the original address
| 0x0A00 | Add a new bit field definition to the original address
2021-06-19 | 0x05C4 | IncreasePVtotal power address
| 0x0667-0x0669 | Add battery summary information address
| 0x0916 | Add voltage drop time address
| 0x0940 | IncreaseBit6
| 0x0961-0x0962 | Increase the frequency address of over and under frequency power crossing point
| 0x1060 | IncreasePCCPower harvesting device configuration address
| Fault4-byte1-bit5 | Add fault bits
2021-08-03 | 0x1098-0x109C | newPIDconfigure address
| 0x110F | newPIDcontrol address
| Fault12-byte1-bit6 | Add fault
2021-08-11 | 0x044C | Change from reserved address to valid serial number address
| 0x0470-0x0476 | new2a valid serial number address, and5reserved addresses
| 0x10A0-0x10A1 | Added PLC enable and configuration address
| 0x10A5-0x10A6 | Added BLE enable and configuration address
| 0x10B0-0x10A4 | RevisePIDEnable and configure addresses
| 0x8027 | Change from reserved address to valid serial number address
| 0x8028-0x802E | new2a factory valid serial number address, and5reserved addresses
| 0x802F-0x8032 | Added peripheral configuration address and peripheral configurationBITCorrespondence table
| 0xA06A | Added remote reset command
| Fault12-byte1-bit7 | newPLCheartbeat failure
2021-08-31 | 0x1108 | Address data type changed to signed
| Fault13,Fault14 | Alarm name change
| 0x0040-0x0043 | Increase the agreement "general" area
| 0x0044 | Increase the protocol version number
2021-09-06 | Fault8-byte1-bit0 Fault8-byte1-bit1 | Added lightning protection fault(DC)and lightning protection failure(AC)
| 0x0044 | Update protocol version definitions
| 0x0045-0x0047 | Add chip code
2021-10-11 | 0x0940 | IncreaseBit7definition
2021-11-03 | 0x1023 | Added Mode Definition: Phase Power Mode
| 0x1034 | language definition
| 0x1061 | Added resonance detection sensitivity register
| 0x1110 | Added mode definition: off-grid mode
| 0x1144-0x1146 | Added Off-Grid Mode Register
| 0x203D-0x203F | Added target chip definitions: PCU (Power Control Unit) and BMS (Battery Management System)
| 0x7000-0x707F | newODMData customization area
| ID91 | Added resonance protectionID
| ID106 | Add serial number model errorID
2021-12-08 | 0x8020 | Address misplacement problem fixed
| 0x1051 | Register definition update
| 0x1057-0x105A | Add lead-acid battery related registers
| 0x100C | Register definition update
2021-12-27 | Fault1-byte1-bit5 | Added voltage unbalance fault
| Fault3-byte0-bit6 | Added arc protection
| Fault3-byte0-bit7 | Add low light detection failure
| Fault6-byte1-bit2 | Changed to resonance protection
| Fault6-byte1-bit3 | Added stream limiting protection for anchors
| Fault7-byte1-bit1 | Add serial number model fault
| Fault12-byte1-bit5 | Delete arc alarm
| PCUFault bit description | Add fault description page
| 0x0404 | add new status
| 0x0466-0x046A | Increase AFCI version
| 0x0510,0x0518,0x0520 | Modify the field to emergency load voltage
| 0x06E3-0x06EC | Increase the internal information register
| 0x0744-0x0763 | add string3,4circuit current
| 0x0784-0x07A1 | Modify the arc information field
| 0x1046 | Update register definitions
| 0x1085-0x1092 | Modify arc configuration fields
| 0x1110 | Added mode definition: generator mode
| 0x2039-0x203C | Added registers to support one-to-many upgrade and silent download
| 0x6000-0x6FFF | newPCUdata area
| 0x7000 | update definition
V1.10 | 0x8019-0x801A | Production management area:0x8019-0x801Atable duplicates, delete duplicate rows
| 0x0466-0x046A | Version update record (line 133 on this page) address0x0477-0x047BCorrection
| Fault12:bit0-5 | The described alarm is changed to protection
| 0x8012-0x8013 | Increase total read and write power generation
| 0x900D | Modification description: the lower 8 bits of all battery pack battery string numbers
| 0x9010 | Modification type: U16 changed to I16
| 0x9079 | Modify the precision, by0.01Change to 0.1
| 0x907B | Increase the total number of strings of battery packs for read-only batteries
| 0x907C | Increase the number of battery cell strings in a single battery pack of the read-only group
| 0x90B8 | Increase the total number of battery packs for read-only batteries
| 0x90B9 | Increase the number of battery cell strings in a single battery pack of the read-only group
| Fault11:bit4-bit6 | Modify fault165-167delete
V1.11 | 0x43B-0x43D | Added Fault28-Fault29 to disable the bit area by default
| Fault28 | Added protocol version error (ARM)
| Fault29:bit0 | Modify the zero-ground voltage is too high (delete Fault0:bit15)
| Fault29:bit1 | Modify PV branch software overcurrent (delete Fault6:bit13)
| 0x1147 | Added dry contact control mode setting
| 0x45E-0x45F | Added BOOT version number (main DSP, secondary DSP)
| 0x2100-0x213F | Added power carrier communication PLC parameter area
| 0x1046 | Added battery parameters - communication protocol 11: action
V1.12 | 0x6048-0x604E | Added MODBUS protocol Added PCU voltage and current calibration coefficient
| 0x11C4-0x11C8 | Added power station communication interruption protection function register
| Fault11-byte0:bit3 | Added fault ID164 "PSCommFault" "Power Plant Communication Fault Shutdown"
| 0x200D | Added: Protocol Settings Register
| 0x8012-0x8013 | Total power generation modified to write only
| 0x1046 | Add battery parameters - communication protocol 11: BTS 5K Modify battery parameters - communication protocol 12: Action
| PCU fault bit Fault3 | Added PCU fault bit bit6: SwBusInstantOCP: Bus software overcurrent; Added PCU fault bit bit8: PackIDErr: PackID error;
V1.13 | 0x0052-0x0054 | Enable reserved address, increase reading of protocol version number (ARM/DSPM/DSPL)
| Fault2.byte1.bit7/Fault9.byte1.bit | Added Fault2.byte1.bit7 neutral point ground fault; Added Fault9.byte1.bit grid relay fault
| 0x066A | Added "Real-time Battery Channels" in the new battery information area
| 0x06ED | Added "Inverter Rated Power", unit 0.1kW, read-only
| 0x60A1-60A2 | Added "Total number of strings/Total number of batteries", read only
| 0x60C5~60C7 | Added the number of the specified number of operations and the corresponding string/battery rated power
| 0x200D | Added 0x0005: solarmax protocol
| 0x1062 | Added CT ratio setting
| 0x1063 | Added hard anti-backflow switch
| 0x102E | Modified description of Italian test S/F
| Fault7-byte1-bit0 Fault11-byte1-bit7 | Modify the description of the fault field, and delete the repetition of the communication fault of the electric meter
| 0x2100-0x213F | Modify power carrier communication PLC parameter area